## Development (hidden)
Date | Revision | Description | Reviewed by | Approved by
| Rev 1.1 | Correction in Group Heating PV calculation
| Rev 1.2 | Correction in Renewable Energy Ratio Calculation for Group Schemes and Heat Pumps tested to EN14511
2021-12-21 | Rev 1.3 | Cooling Calculations and naming changes for HP (see list below) | Antonella Uras NZEB Programme Manager | Antonella Uras NZEB Programme Manager
2023-01-31 | Rev 1.4 | Change in Electricity factors, Fuel tab, as per description document; Vent tab fix in cell H55 (formula for ac/h for positive input vent from loft); Code tab added Cooling | Muiris O'Neill CM Programme Executive | Antonella Uras CM Programme Manager
Heat pumps naming changes v 1.3
Description | Location |  |  |  | Sheet | Cell: | Existing text in the workbook: | Text change in the workbook v1.3 (Cooling development version 0.7)
| Sheet | Cell |  |  | HP | A38 | Test Conditions EN 14825:2013 | Test Conditions I.S. EN 14825
Cooling Calculation | Cooling | All Cells |  |  | HP | A45/A47 | EN 14825:2013 - Table 12 (ASHP) or Table 24 (GSHP) | Source from Ecodesign data or I.S. EN14825 Table 8 for air source. Table 12 for brine or water source. [These table # references are from 2016 version of this standard]
Cooling Calculation | ER1 | Row 36 |  |  | HP | A49/51 | EN 14825:2013 -Table 15 (ASHP) or Table 27 (GSHP) | Source from Ecodesign data or I.S. EN14825 Table 9 for air source. Table 13 for brine or water source. [These table # references are from 2016 version of this standard]
Cooling Calculation | ER1 | Row 57 |  |  | HP | A46/A47 | EN 14825:2013 - Table 6 (AAHP), Table 9 (GAHP), Table 18 (ASHP) or Table 30 (GSHP) | Source from Ecodesign data or I.S. EN14825 Table 10 for air source. Table 14 for brine or water source. [These table # references are from 2016 version of this standard]
Cooling Calculation | ER1 | Row 79 |  |  | HP | A46/A47 | EN 14825:2013 - Table 21 (ASHP) or Table 33 (GSHP) | Source from Ecodesign data or I.S. EN14825 Table 11 for air source. Table 15 for brine or water source. [These table # references are from 2016 version of this standard]
Cooling Calculation | ER2 | Row 59 |  |  | HP | B38 | High Temperature Data is mandatory requirement under Ecodesign Directive (Note its referred to as Medium Temperature Application in Ecodesign directive) | Medium Temperature data is mandatory requirement under Ecodesign Directive (Note this was referred as High Temperature in earlier versions of EN 14825)
Cooling Calculation | ER2 | Row 80 |  |  | HP | B40 | Medium Temperature | Intermediate Temperature
Cooling Calculation | ER2 | Row 110 |  |  | HP | B41 | Very High Temperature | High Temperature
Cooling Calculation | Result | Row 8 |  |  | HP | B43 | Test Conditions EN 14825:2013 | Test Conditions I.S. EN 14825
[5 empty] | HP | A48 | Mid Temperature Application (45oC) | Intermediate Temperature Application (45oC)
[5 empty] | HP | A52 | High Temperature Application (55oC) | Medium Temperature Application (55oC)
[5 empty] | HP | A56 | Very High Temperature Application (65oC) | High Temperature Application (65oC)
[5 empty] | HP | A86 | Capacity of Heat Pump | Hot water Rated Heat output Prated
[5 empty] | HP | A88 | Standby Heat Loss | Standing heat loss of test storage tank
[5 empty] | Heating Calc | A16 | Medium Temperature (oC) | Intermediate Temperature (oC)
[5 empty] | Heating Calc | A17 | High Temperature (oC) | Medium Temperature (oC)
[5 empty] | Heating Calc | A18 | Very High Temperature (oC) | High Temperature (oC)
[5 empty] | Heating Calc | A19 | COP at sink temperature Low Temp (kW/kW) | Low Temperature COP (kW/kW)
[5 empty] | Heating Calc | A20 | COP at sink temperature Medium Temp (kW/kW) | Intermediate Temperature COP (kW/kW)
[5 empty] | Heating Calc | A21 | COP at sink temperature High Temp (kW/kW) | Medium Temperature COP (kW/kW)
[5 empty] | Heating Calc | A22 | COP at sink temperature Very High Temp (kW/kW) | High Temperature COP (kW/kW)
[5 empty] | Heating Calc | A23 | Heating Capacity at Low Temp (kW) | Low Temperature Heating Capacity (kW)
[5 empty] | Heating Calc | A24 | Heating Capacity at Medium Temp (kW) | Intermediate Temperature Heating Capacity (kW)
[5 empty] | Heating Calc | A25 | Heating Capacity at High Temp (kW) | Medium Temperature Heating Capacity (kW)
[5 empty] | Heating Calc | A26 | Heating Capacity at Very High Temp (kW) | High Temperature Heating Capacity (kW)
[5 empty] | Heating Calc | I20 | Taken from Input Sheet Medium Temperature COP | Taken from Input Sheet Intermediate Temperature COP
[5 empty] | Heating Calc | I21 | Taken from Input Sheet High Temperature COP | Taken from Input Sheet Medium Temperature COP
[5 empty] | Heating Calc | I22 | Taken from Input Sheet Very Temperature COP | Taken from Input Sheet High Temperature COP
[5 empty] | Heating Calc | I24 | Taken from Input Sheet Medium Temperature Capacity | Taken from Input Sheet Intermediate Temperature Capacity
[5 empty] | Heating Calc | I25 | Taken from Input Sheet High Temperature Capacity | Taken from Input Sheet Medium Temperature Capacity
[5 empty] | Heating Calc | I26 | Taken from Input Sheet Very Temperature Capacity | Taken from Input Sheet High Temperature Capacity
[5 empty] | Heating Calc | D28 | Blank - C28 has formula that displays Low, Medium, High, Very High | Low, Medium, High, Very High, changed to Low, Intermediate, Medium, High
[5 empty] | Heating Calc | D29 | Blank - C29 has formula that displays Low, Medium, High, Very High | Low, Medium, High, Very High, changed to Low, Intermediate, Medium, High
[5 empty] | Heating Calc | C31-G36 |  | Replacing "Medium" with "Intermediate";"High" with "Medium";"Very High" eith "High" to allow for correct calculation of lower and higher test points

## Cov
Dwelling Energy Assessment Procedure (DEAP)
Irish official method for rating the energy performance of dwellings
Calculation workbook Version 4.2 v1.4
2023-01-01
0 | Rev 1.1 | Correction in Group Heating PV calculation
0 | Rev 1.2 | Correction in Renewable Energy Ratio Calculation for Group Schemes and Heat Pumps tested to EN14511
2021-12-21 | Rev 1.3 | Cooling Calculations and naming changes for HP
2023-01-31 | Rev 1.4 | Change in Electricity factors, Fuel tab, as per description document; Vent tab fix in cell H55 (formula for ac/h for positive input vent from loft); Code tab added Cooling
Disclaimer & Copyright
Copyright to the Calculation Workbook is owned by The Sustainable Energy Authority of Ireland.
Apart from normal data entry, you may not make changes to the Calculation Workbook. You may not make alterations to its
structure, calculation procedures or contained data.
Neither SEAI, its consultants, suppliers nor any of their employees shall be held liable for any loss or
damage caused by the Calculation Workbook.
© 2006-2021 The Sustainable Energy Authority of Ireland. All rights reserved.

## Code
Overview of workbook
Cell shading
(based on Excel's standard colour palette)
Background colours used in data cells on the worksheets signify the following.
| Colour |  | Cell category
| Yellow |  | User inputs
| Blue |  | Main calculated results
| Green |  | Constants
| None |  | Intermediate calculated data
Use of this workbook
A calculation using this workbook should work sequentially through the individual spreadsheets as follows, leading ultimately to the display of results in the ‘Results’ worksheet:
| Worksheet | Main user entry actions |  | Visible calculated outcome
| Proj | Enter administrative details of the project (optional) |  | As entered
| Dims | Enter principal dimensions |  | Total floor area, dwelling volume
| Vent | Enter structural and other ventilation characteristics |  | Ventilation heat loss (components and total), electricity for fans, heat gain from fans
| Win | Enter window and glazed door dimensions, orientations, U values and shading characteristics |  | Glazed area, heat loss, effective area for solar gain, glazing ratio for daylight gain, summer heat gain
| Fab | Enter building element dimensions, U values and thermal bridging characteristics |  | Fabric heat loss, total heat loss coefficient and heat loss parameter for dwelling. Compliance check with Building Regulation L2 (b)
| Wh | Enter water heating system characteristics, including electrical immersion and solar |  | Hot water heat demand, solar hot water pump consumption, primary circuit loss, internal heat gains from hot water
| Light | Enter proportion of fixed lighting outlets that are low energy |  | Annual energy use for lighting, internal seasonal heat gains from lighting, heat gains from all sources
| HtUse | Enter living area fraction and thermal mass category |  | Mean internal temperature, annual ‘useful’ space heat demand from monthly calculations allowing for intermittency, solar and internal heat gain utilisation
| Sh | Enter heating system control category, responsiveness category, heat emission characteristics, pumps and fans |  | Annual space heat demand allowing for control, responsiveness, heat emission and equipment heat gain characteristics
| Cooling | Enter cooling system if present |  | Delivered Energy for Space Cooling
| Er1 | Individual heating systems: Enter space and water heating appliance efficiency and fuel characteristics |  | Annual fuel consumption for space and water heating, CO2 emissions, costs
| Er2 | Community/ group heating schemes: Enter space and water heating appliance efficiency and fuel characteristics |  | Annual fuel consumption for space and water heating, CO2 emissions, costs
| Result | None |  | Annual delivered energy, primary energy, CO2 emissions, costs, comparison with reference dwelling, compliance check with Building Regulation L2 (a)
| RER | None |  | Renewable Energy Ratio calculation
| Fuel | Enter Electricity CO2 and Primary Energy Factors |  | As entered
| SWH | Enter the aperture area, zero loss collector efficiency, collector heat loss coefficient, annual radiation, overshading factor and dedicated solar storage data |  | Solar Domestic Hot Water input
| Summer | Enter air change rate and summer external temperature |  | Threshold Internal Temperature
| HP | Enter Manufacturer, model, test standard, test data of heat pumps, run hours and design flow temperature of heat pumps |  | Efficiency of Space Heating Heat Pump, Water Heatining Heat Pump, Renewable Contribution
| Heating Calc | None |  | Space Heating calculations for Heat Pump
| DHW Calc | None |  | Water Heating calculations for Heat Pump
| Meteorological Data | None |  | Bin data for heat pump calculation

## Proj
Project
Inputs to this sheet are optional.
Project details
Dwelling type
Address
Eircode
MPRN Number
Date of assessment
Type of Rating
Purpose of Rating | -
Is there an Extension?
Year of Construction
Building Regulations | 2019
Developer/owner details
Name
Address
Phone
Email
Assessor details
Name
Title
Company
Phone
Email
Address
Comments
Tables
Dwelling types
-
Ground-floor apartment
Mid-floor apartment
Top-floor apartment
End of Terrace
Mid- terrace
Semi-detached house
Detached house
Maisonette
Basement apartment
Purpose of rating
-
New dwelling for owner occupation
Sale
Private letting
Social housing letting
Grant Support
Major Renovation
Other
Extension
-
Yes
No
Building Regulations Compliance Checking
2019
2011
N/A
Type of rating
-
New-final
New-provisional
Existing

## Dim
Overall dwelling dimensions
| Area | Avg room | Volume
| [m2] | height [m] | [m3]
Ground or lowest floor | 81 | 2.45 | 198.45
First floor |  |  | 0
Second floor |  |  | 0
Third and other floors |  |  | 0
Total floor area [m2] | 81
Dwelling volume [m3] |  |  | 198.45
| [m2] | Fraction
Living area | 40.5 | 0.5

## Vent
Ventilation heat loss | [13 empty] | Reference Building
Openings | [5 empty] | [m3/h] | [ac/h]
Number of chimneys |  |  |  |  | 0 | 0 | [7 empty] | 40
Number of open flues |  |  |  |  | 0 | 0
Number of intermittent fans and passive vents |  |  |  |  | 1 | 10 | [7 empty] | 20
Number of flueless combustion room heaters |  |  |  |  | 0 | 0
Sub-total | [5 empty] | 10 | [7 empty] | 60
Is there a draught lobby on main entrance? |  |  |  | No | 0 |  | 0.05 | [6 empty] | 0.05
Infiltration due to openings | [6 empty] | 0.10039 | [6 empty] | 0.35234
Structural air-tightness | [6 empty] | [ac/h]
Number of storeys in the dwelling | [5 empty] | 2 | 0.1
Has an air permeability test been carried out? |  |  |  |  | Yes | 1
If no (ie. If test has not been done):
| Structure type |  |  |  | Masonry |  | 0.35
| Is there a suspended wooden ground floor? |  |  |  | None |  | 0
| Percentage of windows and doors draughtstripped [%] |  |  |  |  | 100 | 0.05
| Infiltration due to structure - calculated | [5 empty] | 0.5
Else if yes (ie. if test has been done):
Air Tightness Test Reference Number
| Air permeability test in m3/hr/m2 (q50). Follow TGD L guidance. | [5 empty] | 3 | m3/h/m2
| Infiltration due to structure - measured [ac/h] | [5 empty] | 0.15 | ach
End if (ie. end of inputs covered by above "If / Else if" conditions). | [6 empty] | Permeability test carried out and meets guidelines in TGD L? |  |  |  |  | Complies
Infiltration due to structure [ac/h] | [5 empty] | 0.15 | [7 empty] | 0.5
Infiltration rate - 1 [ac/h] | [5 empty] | 0.25039 | [7 empty] | 0.85234
Number of sides sheltered | [5 empty] | 2 | Enter 2 for new dwellings where location is not shown | [6 empty] | 2
Infiltration rate - final [ac/h] | [5 empty] | 0.21283 | [7 empty] | 0.72449
Ventilation method |  |  | Whole-house extract ventilation | [5 empty] | ID | 4 |  |  |  | 1
If "Exhaust Air Heat Pump" what is the Exhaust Air Flow Rate | [5 empty] | 0 | m3/h
Effective air change rate [ac/h] | [5 empty] | 0.5 |  |  |  |  | Heat Pump Flow Rate Ratio | Rhp | N/A | 0.76244
Ventilation heat loss [W/K] | [5 empty] | 32.7443 |  |  |  |  | Hrs of Operation | hrs | N/A | 49.9313
[11 empty] | Mechanical Ventilation Throughput Factor | Fmv | N/A
If mechanical ventilation, other than positive input ventilation from loft, has been selected above:
| Is measured "PCDB" data available? | [5 empty] | Yes | 1
If yes
Manufacturer and model
|  | How many wetrooms (including kitchen)? Is the ventilation ducting flexible/rigid/both? | [5 empty] | Default | Value to be used
|  | Specific fan power [W/(l/s)] |  |  |  |  | 0.2 | 0.8 | 0.2
If balanced whole-house mechanical ventilation with heat recovery:
|  |  | Heat exchanger efficiency [%] |  |  |  |  | 0 | 0
End if
| End if | [6 empty] | Efficiency Adjustment Factor
| Is ducting insulated where outside of insulated dwelling envelope |  |  |  |  | NA | 1 | 1
| Electricity for ventilation fans [kWh/y] |  |  |  |  | 48.4218
| Heat gains from ventilation fans [W] |  |  |  |  | 0
End if
Tables
Ventilation methods | [5 empty] | ID | Effective air change rate | Default SPF
[7 empty] | [ac/h] | [W/(L/s)]
Natural ventilation | [5 empty] | 1 | 0.52265 | 0
Positive input ventilation from loft | [5 empty] | 2 | 0.62343 | 0
Positive input ventilation from outside | [5 empty] | 3 | 0.5 | 0.8
Whole-house extract ventilation | [5 empty] | 4 | 0.5 | 0.8
Balanced whole-house mechanical ventilation, no heat recovery | [5 empty] | 5 | 0.71283 | 2
Balanced whole-house mechanical ventilation with heat recovery | [5 empty] | 6 | 0.71283 | 2
Exhaust Air Heat Pump | [5 empty] | 7 | 0 | 0.26
- | [5 empty] | - | 0 | 0
YesNo
Yes | 1
No | 0
NA | 1
Structural infiltration
Masonry |  | 0.35
Timber or steel frame |  | 0.25
- |  | 0
Suspended timber ground floor
None |  | 0
Yes - sealed |  | 0.1
Yes - unsealed |  | 0.2
- |  | 0
TGD L 2011 pressure test result pass
FALSE
TGD L 2011 pressure test result fail
FALSE
TGD L 2019 pressure test result pass
TRUE
TGD L 2019 pressure test result fail
FALSE
TGD L 2011 or 2019 pressure test carried out: fails
FALSE
TGD L 2011 or 2019 pressure test carried out: passes
TRUE
Note on A4: Chimney ventilation includes effect of associated permanent vent.
Note on A15: "If / Else if / End if" statements occur throughout the workbook. Where the "If" or "Else if" condition does not apply, the inputs it covers will not affect the result. The user need only enter data where the condition applies.
Note on B23: Air changes per hour is taken to be numerically equal to m3/m2.h.
Note on B37: from PCDB website.
Note on C39: As given on "Appendix Q" website.
Note on C40: skavanagh: Text description of MV system

## Win
Windows and other glazed elements | [13 empty] | Reference Building
Enter details of windows or rooflights on each façade or building element (up to 9). See notes below Table 1b.
Totals
Orientation |  |  |  | East/West | South | North | SE/SW | South | North | North | North | Horizontal
Orientation ID |  |  |  | 3 | 5 | 1 | 4 | 5 | 1 | 1 | 1 | 6
Area [m2] |  |  |  | 10.8 | 9 | 0 | [6 empty] | 19.8 | 18.4
Roof window |  |  |  | No | No | No | - | - | - | - | - | -
Heat loss
U-value [W/m2 K] |  |  |  | 0.9 | 0.9 | 0.9 | [7 empty] | 2.2
Is U-value a manufacturer's certified value? |  |  |  | Yes | Yes | Yes | - | - | - | - | - | -
If yes:
Manufacturer and model
| Solar energy transmittance |  |  | 0.6 | 0.6 | 0.6
End if
U-value correction for roof window and/or metal frame if applicable (Table 6a, notes 1 and 2).
Adjusted U-value [W/m2 K] |  |  |  | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 17.82
Adjusted U-value, with curtains [W/m2 K] |  |  |  | 0.86873 | 0.86873 | 0.86873 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.0221
Heat loss [W/K] | [12 empty] | 17.2008 | 37.2059
North facing roof window? |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Passive solar gain
Overshading ID (Table 6d) |  |  |  | 2 | 2 | 2 | [7 empty] | 2
Winter solar access factor |  |  |  | 0.77 | 0.77 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.77
Light access factor |  |  |  | 0.83 | 0.83 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.83
Frame factor (Table 6c) [-] |  |  |  | 0.7 | 0.7 | 0.7 | [7 empty] | 0.7
Window type ID (Table 6b) |  |  |  | 7 | 7 | 7 | [7 empty] | 3
Solar transmittance |  |  |  | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72
Light transmittance |  |  |  | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.8
Incidence angle factor [-] |  |  |  |  | 0.9
Effective collecting area of glazed elements [m2] |  |  |  | 3.1434 | 2.6195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.763 | 6.4266
Orientation | ID | Total window area [m2] |  |  | Effective collecting area [m2]
North | 1 | 0 |  |  | 0
NE/NW | 2 | 0 |  |  | 0
East/West | 3 | 10.8 |  |  | 3.1434 | [8 empty] | 6.4266
SE/SW | 4 | 0 |  |  | 0
South | 5 | 9 |  |  | 2.6195
Horizontal | 6 | 0 |  |  | 0
North roof windows | 1 | 0
Daylighting
Glazing ratio [-] |  |  |  |  | 0.089474 | [8 empty] | 0.095026
Solar gain in summer (optional - for assessment of internal temperature in summer. See 'Summer' worksheet)
Orientation as entered above |  |  |  | East/West | South | North | SE/SW | South | North | North | North | Horizontal
Solar flux for summer period [W/m2] |  |  |  | 111 | 110 | 78 | 115 | 110 | 78 | 78 | 78 | 185
Summer solar access factor (unshaded) |  |  |  | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Shading factor for blinds/curtains (Table P4) |  |  |  | 0.85 | 0.85 | 0.85
Shading factor for overhangs (Tables P5-P6) |  |  |  | 1 | 1 | 1
Shaded summer solar access factor |  |  |  | 0.765 | 0.765 | 0.765 | 0 | 0 | 0 | 0 | 0 | 0
Solar gain for summer period [W/m2] |  |  |  |  | 632.9353
Tables
Table 6b: Transmittance factors for glazing
Type of glazing |  |  | ID | Total solar energy transmittance (for solar gains calculation) | Light transmittance (for daylighting calculation)
Single glazed |  |  | 1 | 0.85 | 0.9
Double glazed (air or argon filled) |  |  | 2 | 0.76 | 0.8
Double glazed (Low-E, hard coat) |  |  | 3 | 0.72 | 0.8
Double glazed (Low-E, soft coat) |  |  | 4 | 0.63 | 0.8
Triple glazed (air or argon filled) |  |  | 5 | 0.68 | 0.7
Triple glazed (Low-E, hard coat) |  |  | 6 | 0.64 | 0.7
Triple glazed (Low-E, soft coat) |  |  | 7 | 0.57 | 0.7
- |  |  | 0 | 0 | 0
Table 6d: Solar and light access factors
Overshading |  | % of sky blocked | ID | Winter solar access factor | Summer solar access factor | Light access factor
Heavy |  | >80% | 4 | 0.3 | 0.5 | 0.5
More than average |  | >60 - 80% | 3 | 0.54 | 0.7 | 0.67
Average or unknown |  | 20 - 60% | 2 | 0.77 | 0.9 | 0.83
Very little |  | <20% | 1 | 1 | 1 | 1
- |  |  | 0 | 0 | 0 | 0
Lists
Yes/No
Yes
No
-
Blind or curtain type |  |  |  | Zblind
Net curtain (covering whole window) |  |  |  | 0.8
Net curtain (covering half window) |  |  |  | 0.9
Dark-coloured curtain or roller blind (note 1) |  |  |  | 0.85
Light-coloured curtain or roller blind (note 1) |  |  |  | 0.6
Dark-coloured venetian blind (note 2) |  |  |  | 0.88
Light-coloured venetian blind (note 2) |  |  |  | 0.7
Dark-coloured external shutter, window closed (note 3) |  |  |  | 0.24
White external shutter, window closed (note 3) |  |  |  | 0.27
Dark-coloured external shutter, window fully open (note 3) |  |  |  | 0.85
White external shutter, window fully open (note 3) |  |  |  | 0.65
Note on A4: Edit unused orientations if different window types on the same façade.
Note on A9: U-value of whoe window including frame. Use manufacturer's certified U-values where available, otherwise take from Table 6a.
Note on B13: If window U-value is manufacturer's certified value, solar energy transmittance of glazing should be manufacturer's certified value also.
Note on N17: Not used in DEAP; used in assessing conformity with guidance in TGD L at end of Fabric sheet.

## Fab
Fabric heat loss | [11 empty] | Reference Building
Enter exposed element details only in rows of the correct 'type' below.
Exposed element type |  |  | Area | U-value | AU | Comment (optional) |  |  | Element type |  | ID
|  |  | [m2] | [W/m2 K] | [W/K] |  |  |  | (for assessing TGD L conformity) |  |  | Area | Uval
Windows/rooflights |  |  | 19.8 | 0.86873 | 17.2008 | [6 empty] | 18.4 | 2.0221
Doors |  |  | 1.85 | 1.5 | 2.775 | [6 empty] | 1.85 | 3
Floor |  |  | 0 | 0 | 0 |  |  |  | No underfloor heating |  | 1 | 0 | 0.25
Floor (type 2) |  |  |  |  | 0 |  |  |  | No underfloor heating |  | 1
Floor (type 3) |  |  |  |  | 0 |  |  |  | No underfloor heating |  | 1
Walls |  |  | 24.3 | 0.13 | 3.159 |  |  |  | Wall relevant for TGD L fabric compliance check |  | 1 | 37.2 | 0.27
Walls (type 2) |  |  | 11.5 | 0.194 | 2.231 |  |  |  | Wall relevant for TGD L fabric compliance check |  | 1
Walls (type 3) |  |  |  |  | 0 |  |  |  | Wall relevant for TGD L fabric compliance check |  | 1
Walls (type 4) |  |  |  |  | 0 |  |  |  | Wall relevant for TGD L fabric compliance check |  | 1
Walls (type 5) |  |  |  |  | 0 |  |  |  | Wall relevant for TGD L fabric compliance check |  | 1
Roof |  |  | 0 | 0 | 0 |  |  |  | Pitched roof - Insulation at ceiling |  | 1 | 0 | 0.16
Roof (type 2) |  |  | 0 | 0 | 0 |  |  |  | Pitched roof - Insulation at ceiling |  | 1
Roof (type 3) |  |  |  |  | 0 |  |  |  | Pitched roof - Insulation at ceiling |  | 1
Roof (type 4) |  |  |  |  | 0 |  |  |  | Pitched roof - Insulation at ceiling |  | 1
Roof (type 5) |  |  |  |  | 0 |  |  |  | Pitched roof - Insulation at ceiling |  | 1
Total area of elements [m2] |  |  | 57.45 | [8 empty] | Ok
Heat loss via plane elements [W/K] |  |  |  |  | 25.3658 | [6 empty] | 52.7999
Factor for thermal bridging at element junctions, 'y' [W/m2 K] | [5 empty] | 0.05 | [5 empty] | 0.11
Thermal bridging [W/K] |  |  |  |  | 2.8725 | [6 empty] | 6.3195
Fabric heat loss [W/K] |  |  |  |  | 28.2383 | [6 empty] | 59.1194
Total heat loss
Heat loss coefficient [W/K] |  |  |  |  | 60.9825 |  |  |  | Chart data |  |  | 109.0507
Heat loss parameter, HLP [W/K m2] |  |  |  |  | 0.75287 |  |  |  | Fabric | 28.2383
[9 empty] | Ventilation | 32.7443
Chart data
[8 empty] | Floors | 0
[8 empty] | Walls | 5.39
[8 empty] | Roofs | 0
[8 empty] | Openings | 19.9758
[8 empty] | Junctions | 2.8725
|  |  |  | Conformity with guidance within TGD L | 2019
For information only; not part of DEAP. Relevant for new-build.
Maximum average U-values of element types (TGD L, Section 1.3.2.2 and Table 1, Column 2). *
Note that U-values will generally need to be better than these limits in order for dwelling to comply with MPEPC and MPCPC requirements.
[5 empty] | TGD L | Area | Average
Category | Type |  |  | ID | limit | of type | U-value
[5 empty] | [W/m2 K] | [m2] | [W/m2 K]
Roofs | - |  |  | 0
| Pitched roof - Insulation at ceiling |  |  | 1 | 0.16 | 0 | - | -
| Pitched roof - Insulation on slope |  |  | 2 | 0.16 | 0 | - | -
| Flat roof |  |  | 3 | 0.2 | 0 | - | -
Walls
| Walls |  |  |  | 0.18 | 35.8 | 0.15056 | Complies
Floors | - |  |  | 0
| No underfloor heating |  |  | 1 | 0.18 | 0 | - | -
| Underfloor heating |  |  | 2 | 0.15 | 0 | - | -
Openings
Total opening area (windows/rooflights/doors) as % of total floor area | [6 empty] | 0.26728
Average U-value of openings [W/m2 K] | [6 empty] | 0.95127
Complies
Maximum elemental U-values (TGD L, Section 1.3.2.2 and Table 1, Column 3)
[W/m2 K] |  |  |  | TGD L | Max value
|  |  |  | limit | in dwelling
Roofs |  |  |  | 0.3 | 0 | Complies
Walls |  |  |  | 0.6 | 0.194 | Complies
Floors |  |  |  | 0.6 | 0 | Complies
External doors, windows and rooflights |  |  |  | 3 | 1.5 | Complies
*caveat fot TGD L 1.3.2.3 not detailed in this workbook.
For info/checking
Facade area, including windows/doors |  |  |  | 57.45
Gross roof area, including rooflights |  |  |  | 0
Total exposed floor area |  |  |  | 0
|  |  | Sum | 57.45
Subsidiary calcs for TGD L compliance
Gross wall+roof area | [5 empty] | 57.45
Excess of Reference opening area over gross wall area | [5 empty] | 0
Walls relevant for TGD L checking
Wall not relevant for TGD L fabric compliance check | 0
Wall relevant for TGD L fabric compliance check | 1
Windows compliance checking
2019 | Complies
2011 | Complies
List of walls
| effective area | relevant U value for wall | relevant AU for wall
Walls | 24.3 | 0.13 | 3.159
Walls (type 2) | 11.5 | 0.194 | 2.231
Walls (type 3) | 0 | 0 | 0
Walls (type 4) | 0 | 0 | 0
Walls (type 5) | 0 | 0 | 0
Note on A6: Use manufacturer's certified U-values where available, otherwise take from Table 6a.
Note on B6: If there are different types of opaque door, enter total area and average U-value.
Note on A7: Ground floor or exposed floor.
Note on A22: Default 0.15. 0.08 for new dwellings whose details conform with "Acceptable Construction Details". See Appendix K.
Note on A28: For information only.

## WH
Water heating | [13 empty] | Reference Building
Standard number of occupants, N |  |  |  |  | 2.4816
No of (Mixer + Electric) Showers within Dwelling |  |  |  |  | 1
Is a Bath present within Dwelling |  |  |  |  | Yes
Hot Water Usage in litres per day for Mixer Showers
| No of Showers Taken |  |  |  | 1.7667
|  | Is flow rate known | Type of System |  | Flow Restrictor | Known Flow Rate l/min | Flow Rate l/min | Warm Water Use V warm, I (litre) | Warm Water Use Vd warm, I (litre/day) | fhot, shower | Vhot,i | No of Electric Showers
| Shower 1 | No | Vented hot water system + pump |  | Yes | 7 | 6 | 36 | 63.6013 | 0.71948 | 45.76 | 0 | Flow Rate | 12 | l/min
| Shower 2 | No | Vented hot water system |  | No | 7 | 7 | 42 | 0 |  | 0 | 0 | Vd | 127.2026
| Shower 3 | Yes | Vented hot water system |  | No | 7 | 7 | 42 | 0 |  | 0 | 0 | Hot Water Use | 91.52 | litres
| Shower 4 | Yes | Vented hot water system |  | No | 7 | 7 | 42 | 0 |  | 0 | 0
| Shower 5 | Yes | Vented hot water system |  | No | 7 | 7 | 42 | 0 |  | 0 | 0
0
[10 empty] | Hot Water usage in litres per day for Mixed Showers | 45.76 | litres
PCDB characteristics
|  | Associated with | Waste Water Heat Recovery Present | Efficiency, n | Utilisation factor, UF | Warm Water Use Vd warm, I (litre/day) | Energy Content of Warm Water Q (kWh/yr) | Energy Savings (kWh/yr)
| WWHR1 | Shower 1 | No | 0 | 0 | 63.6013 | 598.7462 | 0
| WWHR2 | Shower 2 | No | 0 | 0 | 0 | 0 | 0
| WWHR3 | Shower 3 | No |  |  | 0 | 0 | 0
| WWHR4 | Shower 4 | No |  |  | 0 | 0 | 0
| WWHR5 | Shower 5 | No |  |  | 0 | 0 | 0
[7 empty] | Total WWHR Saving | 0 | kWh/yr
Electricity from Electrical Showers
| Nes |  |  |  | 0
| Electrical Consumption from Electric Shower(s) |  |  |  | 0 | kWh
Is water use target (hot and cold) ≤ 125 l/p/d |  |  |  |  | No
Hot Water Usage in litres per day for Baths
| No of Baths Taken |  |  |  | 0.5126 | [8 empty] | 0.5126
| V warm, bath |  |  |  | 37.42 | [8 empty] | 37.42
| fhot, bath |  |  |  | 0.74498
| Hot Water usage in litres per day for Bath |  |  |  | 27.8773 | litres | [7 empty] | 27.8773
Hot Water usage in litres per day for Other Purposes |  |  |  |  | 38.3193 | litres | [7 empty] | 38.3193
Daily hot water usage, Vd, average, excluding Electric Showers |  |  |  |  | 111.9566 | litres | [7 empty] | 157.7165
Energy Content of hot water used |  |  |  |  | 1755.5692 | kWh/yr | [7 empty] | 2473.1225
Hot water energy requirement at taps |  |  |  |  | 1492.2338 | kWh/yr | [7 empty] | 2102.1541
Water heating system
Are there distribution losses? |  |  |  | Yes | 1 |  |  | Select no for instantaneous heating at point of use.
Distribution loss [kWh/y] | [5 empty] | 263.3354 |  | Select yes if community heating | [5 empty] | 370.9684
Are there storage losses? |  |  |  | Yes | 1
If yes:
| Water storage volume [litres] |  |  |  |  | 180 |  | Include any solar storage within the same cylinder. | [5 empty] | 120
For community heating, if no tank, enter 110 litre cylinder with 50 mm factory applied insulation.
| Is manufacturer's declared loss factor available? |  |  |  |  | No | 0
If yes
Manufacturer and model name
|  | Manufacturer's declared loss factor [kWh/day] |  |  |  |  | 1.2
|  | Storage loss - 1 [kWh/y] |  |  |  |  | 438
Else if no
|  | Insulation type on hot water store |  |  |  | Factory insulated |  | ID | 1
|  | Insulation thickness [mm] |  |  |  |  | 100 | [6 empty] | 35
|  | Hot water storage loss factor [kWh/l d] |  |  |  |  | 0.010288 | [6 empty] | 0.019103
|  | Volume factor |  |  |  |  | 0.87358 | [6 empty] | 1
|  | Storage loss - 2 [kWh/y] |  |  |  |  | 590.4984 | [6 empty] | 836.6923
End if
| Storage loss - 3 [kWh/y] |  |  |  |  | 590.4984
| Temperature factor unadjusted (Table 2) |  |  |  |  | 0.6 | [7 empty] | 0.6
| Temperature factor multiplier (from Table 2 notes) |  |  |  |  | 0.9 | 0.54 | [6 empty] | 0.9
End if
Storage loss - 4 [kWh/y] |  |  |  |  | 318.8691 | [8 empty] | 451.8138
Is there a solar water heating system? |  |  |  |  | No | 0
If yes:
Complete 'SWH' worksheet at this point.
| Solar DHW input, Qs [kWh/y] |  |  |  |  | 0
| Dedicated solar storage contained within cylinder |  |  |  |  | 0
| Is solar water heating pump PV powered? |  |  |  | No | 0
| Electricity consumption of SWH pump [kWh/y] |  |  |  |  | 0
End if
Storage loss - final (adjusted for dedicated solar storage) [kWh/y] | [5 empty] | 318.8691
Primary circuit loss [kWh/y] (Table 3) | [5 empty] | 360 | [7 empty] | 610
Primary circuit loss adjusted for occupancy [kWh/y] | [5 empty] | 291.6703 | [7 empty] | 494.219
Additional loss for combi boiler [kWh/y] (Table 3a) | [8 empty] | Leave blank if not a combi boiler
Electricity consumption of electric keep-hot facility of combi boiler [kWh/y] (Table 4f) | [8 empty] | Leave blank if not applicable
Is hot water storage indoors or in group heating scheme? | [6 empty] | Yes | 1
Is supplementary electric immersion heating used in summer? | [6 empty] | No | 0 | fraction | 0
Solar input to main system [kWh/y] |  |  |  |  | 0
Solar input to supplementary system [kWh/y] |  |  |  |  | 0
WWHRS input to main system [kWh/y] |  |  |  |  | 0
WWHRS input to supplementary system [kWh/y] |  |  |  |  | 0
Output from main water heater [kWh/y] |  |  |  |  | 2366.1086 | [8 empty] | 3419.1554
Output from supplementary heater [kWh/y] |  |  |  |  | 0 |  |  | Breakdown of output from water heater | [5 empty] | 0
Heat gains from water heating system [kWh/y] |  |  |  |  | 1072.1583 |  |  | HW use | 1492.2338 |  |  |  |  | 1579.1395
|  |  | [W] |  | 122.3925 |  |  | Distribution | 263.3354 |  |  |  |  | 180.2671
[8 empty] | Storage | 318.8691
Solar fraction [%] |  | 0 | [5 empty] | Primary c | 291.6703
[8 empty] | Combi b | 0
[8 empty] | Solar input | 0
Tables
YesNo
Yes | 1
No | 0
- | 0
Cylinder insulation
Factory insulated |  | 1
Loose jacket |  | 2
None |  | 2
- |  | 2
Insulation thickness
100
SAP Table J4 Shower Flow Rates and Rated Power
| Default flow rate (l/min) | Default Power (kW)
Vented hot water system | 7
Vented hot water system + pump | 12
Unvented hot water system | 11
Instantaneous electric shower (vented or unvented) | 0 | 9.3
SAP Table 1a: No of days in month
Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual
31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | 365
SAP 10 Table J1: Cold Water Temperatures
Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Annual
7.1 | 8.2 | 9.4 | 13.4 | 15.3 | 17.6 | 18.2 | 17.3 | 16.1 | 13.5 | 10.3 | 6.8 | 12.7868
SAP Table J3 Temperature Rise of the hot water drawn off
Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | annual
41.2 | 41.4 | 40.1 | 37.6 | 36.4 | 33.9 | 30.4 | 33.4 | 33.5 | 36.3 | 39.4 | 39.9 | 37
[16 empty] | 41.2 | 41.4 | 40.1 | 37.6 | 36.4 | 33.9 | 30.4 | 33.4 | 33.5 | 36.3 | 39.4 | 39.9 | 37
Note on A3: Includes distribution loss.
Note on F13: SEAI: Flow Restrictor flow rate is fixed at 6 l/min
Note on I13: SEAI: Based on 6 min Shower
Note on B83: Select 'No' if powered by mains electricity

## Light
Lighting | [8 empty] | Reference Building
Calculation is annual rather than monthly
Annual Base Lighting Requirement | [5 empty] | ɅB | 8149.7397 | klmh/year
Fixed Lighting Requirement | [5 empty] | Ʌreq | 5224.095 | klmh/year
Reference fixed lighting capacity upper limit | [5 empty] | CLref | 26730 | lm
Lighting Design
| Is Lighting Design Known |  |  | Yes
If Yes,
| Lamp | Lamp Power (Watts) | Is lamp efficacy known | Type of Lamp | Lumen /Watt | Lumen /Watt | Lumen
| 1 | 324 | Yes | LEDs/ CFL | 94 | 94 | 30456
| 2 |  | No | Incandescent |  | 11.2 | 0
| 3 |  | No | Incandescent |  | 11.2 | 0
| 4 |  | No | Incandescent |  | 11.2 | 0
| 5 |  | No | Incandescent |  | 11.2 | 0
|  | 324 |  |  |  | CLfixed | 30456 | lm
If No,
|  | Lamp | No of Lamps | Type of Lamp | Lumen /Watt
|  | 1 | 0 | Linear flourescent | 80.5
|  | 2 | 0 | LEDs/ CFL | 66.9
|  | 3 |  | Halogen LV | 26.1
|  | 4 |  | Halogen lamps | 15.7
|  | 5 |  | Incandescent | 11.2
|  |  | 0 | Average Efficacy | #DIV/0! | Clfixed |  | lm
[6 empty] | Clfixed | 30456 | lm
| Fixed lighting provision |  |  |  |  | Ʌprov | 5952.3022 | klmh/year
| Top Up Lighting requirement |  |  |  |  | Ʌtopup | 0 | klmh/year
| Average Efficacy |  |  |  |  | ɛfixed | 94
| Energy Required for fixed lighting |  |  |  |  | EL,fixed | 63.3224 | kWh/year
| Energy Required for top up lighting |  |  |  |  | EL,topup | 0 | kWh/year
| Energy Required for portable lighting |  |  |  |  | EL,portable | 122.6313 | kWh/year
| Annual energy used for lighting, EL [kWh/y] |  |  |  |  | EL | 185.9537 | kWh/year
| Basic energy consumption for lighting [kWh/y] |  |  |  |  | EL,B | 727.6553 | kWh/year
Glazing ratio | [5 empty] | 0.089474 |  |  | 0.095026
Correction factor C2 | [5 empty] | 0.96152 |  |  | 0.96
Annual energy used for lighting, EL [kWh/y] | [5 empty] | 185.9537 |  |  | 698.5491
Internal gains from lighting during heating season [kWh/hs] | [5 empty] | 142.2546 |  |  | 534.3901
|  |  |  | [W] |  | 24.3921 |  |  | 91.6307
Internal gains not from space heating system
[W]
Lighting |  |  |  | 24.3921 |  |  |  |  | 91.6307
Water heating |  |  |  | 122.3925 |  |  |  |  | 180.2671
Metabolic |  |  |  | 124.0781
Appliances and cooking |  |  |  | 181.3497
Mechanical ventilation system |  |  |  | 0 |  |  |  |  | 0
Heat loss to the cold water network [W] |  |  |  | -36.3341
Net internal gains [W] |  |  |  | 415.8782 |  |  |  |  | 540.9914
SAP 2016 Table L1: Default luminous efficacy for lamp types
Lamp Type | Lumens/Watt
Linear flourescent | 80.5
LEDs/ CFL | 66.9
Halogen LV | 26.1
Halogen lamps | 15.7
Incandescent | 11.2

## HtUse
Space heat use | [14 empty] | Reference Building
Required internal temperature
Required temperature of living area during heating hours [C] | [5 empty] | 21
Required temperature of rest of dwelling during heating hours [C] | [5 empty] | 18
Living area fraction [-] | [5 empty] | 0.5
Required mean internal temperature during heating hours [C] | [5 empty] | 19.5
Internal heat capacity
Thermal mass category of dwelling |  |  |  | Medium | [10 empty] | Medium
[6 empty] | UF | IH | [7 empty] | UF | IH
Internal heat capacity of dwelling [MJ/K per m2 floor area] | [5 empty] | 0.2 | 0.11 | [7 empty] | 0.2 | 0.11
|  |  | [MJ/K] |  |  | 16.2 | 8.91 | [7 empty] | 16.2 | 8.91
For calculation of utilisation factor for gains
Time constant of dwelling [h] | [5 empty] | 73.7916 | [8 empty] | 41.2652
Parameter 'a0' | [5 empty] | 1
Reference time constant of building [h] | [5 empty] | 15
Parameter 'a' | [5 empty] | 5.9194 | [8 empty] | 3.751
For calculation of adjusted temperature due to intermittent heating
Time constant of dwelling [h] | [6 empty] | 40.5854 | [7 empty] | 22.6959
Mean external temperature for heating season [C] | [6 empty] | 7.625
Length of one unheated period [h] | [6 empty] | 8
Number of unheated periods per week | [6 empty] | 14
[7 empty] | Unheated | Heated
Hours per week | [6 empty] | 112 | 56
Heat loss from dwelling during one unheated period [MJ] | [6 empty] | 18.9292 | [7 empty] | 31431056.0944
Mean internal temp for one unheated period to give this heat loss [C] | [6 empty] | 18.4029 | [7 empty] | 17.6328
Mean internal temperature for week (and for heating season) [C] | [6 empty] | 18.7686 | [7 empty] | 18.2552
Intermittency temperature factor [-] | [6 empty] | 0.93841 | [7 empty] | 0.89517
Solar gains | [13 empty] | Avg for htg
Month |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | season | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Orientation
North |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NE/NW |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E/W |  | 1.3831 | 2.7662 | 4.7466 | 7.0413 | 9.0531 | 9.116 | 8.4244 | 7.67 | 5.8782 | 3.7093 | 1.7603 | 1.1631 |  | 2.8277 | 5.6554 | 9.7042 | 14.3956 | 18.5086 |  |  |  |  | 7.5834 | 3.5989 | 2.3778
SE/SW |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
South |  | 3.1958 | 5.0557 | 6.2083 | 6.968 | 7.4919 | 6.9942 | 6.7846 | 6.968 | 6.706 | 5.8416 | 4.0603 | 3.0125
Horiz |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total solar gains [kWh/d] |  | 4.579 | 7.8219 | 10.9549 | 14.0093 | 16.545 | 16.1102 | 15.209 | 14.638 | 12.5843 | 9.5508 | 5.8206 | 4.1755
| [W] | 190.7898 | 325.9144 | 456.4548 | 583.7208 | 689.3756 | 671.2571 | 633.7104 | 609.9162 | 524.3446 | 397.9518 | 242.5257 | 173.9811 | 382.5893 | 117.8211 | 235.6422 | 404.3406 | 599.8164 | 771.1926 |  |  |  |  | 315.9747 | 149.9541 | 99.0768
Total gains [W] |  | 606.6681 | 741.7927 | 872.3331 | 999.5991 | 1105.2539 | 1087.1354 | 1049.5886 | 1025.7945 | 940.2228 | 813.83 | 658.404 | 589.8594 | 798.4675 | 658.8125 | 776.6336 | 945.332 | 1140.8079 | 1312.184 |  |  |  |  | 856.9661 | 690.9455 | 640.0682
Heat use
Mean external temperature [C] |  | 5.3 | 5.5 | 7 | 8.3 | 11 | 13.5 | 15.5 | 15.2 | 13.3 | 10.4 | 7.5 | 6
Adjusted internal temperature [C] |  | 18.6254 | 18.6377 | 18.7301 | 18.8102 | 18.9765 | 19.1304 | 19.2536 | 19.2352 | 19.1181 | 18.9395 | 18.7609 | 18.6685 | 18.7686 | 18.0115 | 18.0324 | 18.1897 | 18.3259 | 18.609 |  |  |  |  | 18.5461 | 18.2421 | 18.0848
Heat loss [W] |  | 812.6156 | 801.1704 | 715.3307 | 640.9363 | 486.4249 | 343.3587 | 228.9058 | 246.0738 | 354.804 | 520.7607 | 686.7174 | 772.5571 | 679.5641 | 1386.1948 | 1366.6709 | 1220.2419 | 1093.3367 | 829.7645 |  |  |  |  | 888.3361 | 1171.4322 | 1317.8612
Gain/Loss ratio [-] |  | 0.74656 | 0.92589 | 1.2195 | 1.5596 | 2.2722 | 3.1662 | 4.5852 | 4.1686 | 2.65 | 1.5628 | 0.95877 | 0.76352 |  | 0.47527 | 0.56827 | 0.77471 | 1.0434 | 1.5814 |  |  |  |  | 0.96469 | 0.58983 | 0.48569
Utilisation factor [-] |  | 0.94822 | 0.88626 | 0.75895 | 0.62382 | 0.43818 | 0.3156 | 0.21807 | 0.23985 | 0.37663 | 0.62271 | 0.87285 | 0.94337 | 0.7618 | 0.96681 | 0.94438 | 0.87692 | 0.77242 | 0.58536 |  |  |  |  | 0.80347 | 0.93836 | 0.9646
Useful gains [W] |  | 575.2562 | 657.4177 | 662.0585 | 623.5706 | 484.3033 | 343.1028 | 228.884 | 246.0338 | 354.1132 | 506.779 | 574.69 | 556.4531 | 580.066 | 636.9474 | 733.4382 | 828.9842 | 881.1865 | 768.1017 |  |  |  |  | 688.5478 | 648.358 | 617.4085
Heat use [W] |  | 237.3594 | 143.7526 | 53.2722 | 17.3657 | 2.1215 | 0.25596 | 0.021774 | 0.039989 | 0.69084 | 13.9818 | 112.0275 | 216.104 | 99.4981 | 749.2473 | 633.2327 | 391.2576 | 212.1502 | 61.6628 |  |  |  |  | 199.7883 | 523.0742 | 700.4527
Days per month |  | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Heat use [kWh] |  | 176.5954 | 96.6018 | 39.6345 | 12.5033 | 1.5784 | 0.18429 | 0.016199 | 0.029752 | 0.49741 | 10.4024 | 80.6598 | 160.7814 |  | 557.44 | 425.5324 | 291.0957 | 152.7482 | 45.8771 |  |  |  |  | 148.6425 | 376.6134 | 521.1368
Heat use [kWh/y] |  | Heating season Oct-May |  |  | 578.757 | [9 empty] | 2519.0861
|  | Full year |  |  | 579.4847
Data for chart | [13 empty] | total
Useful internal gains [W] |  | 394.345 | 368.5743 | 315.6314 | 259.4335 | 182.2307 | 131.2523 | 90.6907 | 99.7472 | 156.6309 | 258.971 | 363.0006 | 392.3253 | 3012.8328
Useful solar gains [W] |  | 180.9112 | 288.8434 | 346.4271 | 364.1371 | 302.0726 | 211.8505 | 138.1934 | 146.2866 | 197.4823 | 247.808 | 211.6893 | 164.1278 | 2799.8293
Climate data
Table 1a: Mean external temperature [C]
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Oct-May | Year
Te | 5.3 | 5.5 | 7 | 8.3 | 11 | 13.5 | 15.5 | 15.2 | 13.3 | 10.4 | 7.5 | 6 | 7.625 | 9.875
Table 1b: Monthly means of daily global radiation on surfaces [kWh/m2 day]
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Oct-May | Year
North | 0.27 | 0.51 | 0.91 | 1.36 | 1.89 | 2.12 | 1.94 | 1.57 | 1.06 | 0.61 | 0.33 | 0.2 | 0.76 | 1.0642
NE/NW | 0.27 | 0.53 | 1.02 | 1.68 | 2.34 | 2.49 | 2.28 | 1.92 | 1.29 | 0.69 | 0.33 | 0.2 | 0.8825 | 1.2533
E/W | 0.44 | 0.88 | 1.51 | 2.24 | 2.88 | 2.9 | 2.68 | 2.44 | 1.87 | 1.18 | 0.56 | 0.37 | 1.2575 | 1.6625
SE/SW | 0.94 | 1.53 | 2.05 | 2.6 | 3.02 | 2.88 | 2.74 | 2.69 | 2.35 | 1.84 | 1.19 | 0.87 | 1.755 | 2.0583
South | 1.22 | 1.93 | 2.37 | 2.66 | 2.86 | 2.67 | 2.59 | 2.66 | 2.56 | 2.23 | 1.55 | 1.15 | 1.9963 | 2.2042
Horiz | 0.64 | 1.31 | 2.31 | 3.58 | 4.77 | 4.86 | 4.52 | 3.96 | 2.81 | 1.64 | 0.84 | 0.5 | 1.9487 | 2.645
Number of days in heating season |  |  |  | 243
Table: Internal heat capacity
Category |  | AmAf | Heat capacity per unit floor area [MJ/m2 K]
|  | [-] | UF | IH
Low |  | 0 | 0.07 | 0.07
Medium-low |  | 0.5 | 0.14 | 0.09
Medium |  | 1 | 0.2 | 0.11
Medium-high |  | 2 | 0.32 | 0.15
High |  | 3.5 | 0.5 | 0.2
- |  | 1 | 0.2 | 0.11
Note on G10: For utilisation factor calculation.
Note on H10: For intermittent heating calculation.

## SH
Space heating system | [10 empty] | Reference Building
Control and responsiveness
Temperature adjustment (Table 4e), where appropriate [C] |  |  |  | 0
Adjusted living area temperature [C] |  |  |  | 21 | [6 empty] | 21
Heating system control category (Table 4e) |  |  |  | 3 | Enter category from 1 to 3 | [5 empty] | 2
Temperature in rest of dwelling during heating hours [C] |  |  |  | 18 | [6 empty] | 18.5
Mean internal temperature during heating hours [C] |  |  |  | 19.5 | [6 empty] | 19.75
Heating system responsiveness category (Table 4a or 4d) |  |  |  | 1 | Enter category from 1 to 5 | [5 empty] | 1
| Responsiveness factor [-] |  |  | 0 | [6 empty] | 0
Background temperature [C] |  |  |  | 7.625 | [6 empty] | 7.625
Mean internal temperature [C] |  |  |  | 18.7686 | [6 empty] | 18.479
Additional heat emission due to non-ideal control and responsiveness [kWh/y] |  |  |  | 0 | [6 empty] | 142.329
Gross heat emission to heated space [kWh/y] |  |  |  | 578.757 | [6 empty] | 2661.4151
Pumps/fans
Note: for group/community heating scheme, no pumps, fans or warm air system should be specified.
|  |  |  | Enter | If present, |  | Total Electricity | If present, | Heat gain | Default
Equipment |  |  |  | number | is there a room |  | consumption | inside | [W] | Electricity
|  |  |  | present | thermostat? |  | [kWh/y] | dwelling? |  | consumption
Central heating pump (supplying hot water to radiators or underfloor system) |  |  |  | 1 | Yes |  | 52 | Yes | 10 | 130
Oil boiler - pump (supplying oil to boiler and flue fan) |  |  |  |  | - |  | 0 | - | 0
Gas boiler - flue fan (if fan assisted flue) |  |  |  | 0 |  |  | 0 |  | -
Is there a warm air heating system or fan coil radiators present? |  |  | No | 0 |  |  | 0 |  | 0
[6 empty] | Totals | 52 |  | 10 |  | 175 | 10
Gains from fans and pumps associated with space heating system [kWh/y] | [6 empty] | 58.32 |  |  |  | 58.32
Average utilisation factor, Oct-May | [6 empty] | 0.7618 |  |  |  | 0.85654
Useful heat gain | [6 empty] | 44.4279 |  |  |  | 49.9535
Net heat emission to heated space [kWh/y] | [6 empty] | 534.3291 |  |  |  | 2611.4616
Emission efficiency
Is there underfloor heating in ground or exposed floor? | [5 empty] | - | 0
If yes, U-value of this floor [W/m2 K]
Proportion of heating system output from this floor | [6 empty] | 0.66667
Additional heat loss [kWh/y] | [6 empty] | 0
Annual space heating requirement [kWh/y] | [6 empty] | 534.3291 |  |  |  | 2611.4616
Type of main heating system |  | Individual system |  |  | 1
If individual system, go to 'ER1' sheet; if group system, go to 'ER2' sheet.
Tables
Control category | Delta T
1 | 1.2
2 | 0.5
3 | 0
0 | 1.2
YesNo
Yes | 1
No | 0
- | 0
System type
Individual system |  | 1
Group / community heating scheme |  | 2
- |  | 1
Note on A9: For micro-CHP, use Appendix N to determine value.
Note on A14: Includes heat from heating-system pumps/fans.
Note on K21: Tooltip: refer to DEAP table 4f
Note on A24: Select 'No' if whole-house mechanical ventilation.
Note on A30: Excludes heat from heating-system pumps/fans.
Note on A34: Reference appropriate value on 'Fabric' sheet.

## Cooling
Cooling system | [15 empty] | Reference Building | Notes for DEAP SW and guidance development
Is fixed cooling present | [6 empty] | No | [9 empty] | Energy used is only calculated if fixed cooling is present. If no fixed cooling present, the Area Cooled is set to 0.
Area of Dwelling Cooled (total floor area) | [6 empty] | 0 | m2 | [7 empty] | No cooling in reference building | Set to TFA if fixed cooling is present, no input required.
Make(s) of cooling system | [6 empty] | Make |  | Model(s) of cooling system |  |  | Model |  |  |  |  | This should be linked in the DEAP software to HARP for heat pumps/air conditioners. Default allowed, see SEER value below.
Cooling System Seasonal Energy Efficiency ratio | [6 empty] | 2.16 | [9 empty] | SEER should come from the Ecodesign data through HARP. Deafult for "unknown" to be set to 2.16 in line with the minimum Ecodesign efficiency from 01/01/2013. If more than one air conditioner is present, the SEER should be calculated as the average SEER of the units installed.
Cooling System Fuel | [6 empty] | electricity | [9 empty] | Electricity is default fuel, reduced set of fuels to be available
|  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Days in Month |  | Jun: 30; Jul: 31; Aug: 31
Internal Temperature |  | Jun: 24; Jul: 24; Aug: 24
External Temperature |  | 5.3 | 5.5 | 7 | 8.3 | 11 | 13.5 | 15.5 | 15.2 | 13.3 | 10.4 | 7.5 | 6
Heat Loss Rate Lm [W] |  | Jun: 640.3165; Jul: 518.3514; Aug: 536.6462
τ - Time Constant [h] |  | Jun: 73.7916
a |  | Jun: 5.9194
Gains (internal gains)[W] |  | Jun: 1087.1354; Jul: 1049.5886; Aug: 1025.7945 |  |  |  | Note for DEAP Manual: these are internal gains expected in the hot season, i.e. not from space heating.
ϒ |  | Jun: 1.6978; Jul: 2.0249; Aug: 1.9115
Utiliation factor for loss ŋm |  | Jun: 0.98162; Jul: 0.99217; Aug: 0.98958
Useful loss ŋmxLm |  | Jun: 628.548; Jul: 514.2916; Aug: 531.0559
Space Cooling requirement for month, whole dwelling, continuous (kWh) = 0.024 x (Gains - Useful loss) x days
|  | Jun: 330.1829; Jul: 398.261; Aug: 368.0855; Dec: Total | 1096.5294
Cooling fraction (assumed to be whole house) | [13 empty] | 0 |  |  | Calculated from cooling area (TFA), the fraction is not an input. | bar: Dec
Intermittency Factor |  | Dec: fintermittent | 0.25 |  |  | To note in DEAP Manual: As per SAP 6 hours per day are assumed.
Space Cooling Requirement |  | Dec: Q cool | 0 | kWh/yr
Delivered Energy for Space Cooling [kWh/yr] | [13 empty] | 0 | kWh/yr
Delivered Energy for Space Cooling per m2 [kWh/m2/y] | [13 empty] | 0 | kWh/yr
Constants
Internal temperature for cooling | 24
Fuel list for cooling
mains gas
bulk LPG (propane or butane)
bottled LPG
electricity

## ER1
Energy requirements - individual heating systems | [12 empty] | Heat Pump Present |  | Notes for DEAP SW and guidance development | [7 empty] | Reference Building
TRUE
Space Heating | [7 empty] | Type of Heating System |  |  | Airflow Volume |  | Efficiency of Heat Pump
Efficiency of main heating system [%] (from HARP or from Table 4a or 4b) | [7 empty] | Heat Pump | 91.3 | [%] | 0 | m3/h | 398.8614 | [%]
Manufacturer and model name main space heating | [7 empty] | Complete tab HP |  |  |  |  | % Renewables
Efficiency adjustment factor from Table 4c [-] | [8 empty] | 1 | enter 1 if not applicable |  |  | 100% | [%]
Adjusted efficiency of main heating system [%] | [8 empty] | 398.8614 |  |  |  | Space Heating Demand from Heat Pump | [9 empty] | 78
Fraction of heat from secondary / supplementary system (from Table 7, Table 10 or Appendix F) | [12 empty] | 534.3291 | kWh | [8 empty] | 0.1
Efficiency of secondary / supplementary system [%] (from Table 4a or Appendix E) | [8 empty] | 0 | [%] | [12 empty] | 30
Energy required for main space heating system [kWh/y] | [8 empty] | 133.9636 | [13 empty] | 3013.2249
Energy required for secondary space heating [kWh/y] | [8 empty] | 0 |  |  |  | Heat Pump Present | [9 empty] | 887.1384
Manufacturer and model name secondary space heating | [12 empty] | TRUE
Water heating | [10 empty] | Airflow Volume |  | Efficiency of Heat Pump
Efficiency of main water heater [%] (from HARP or from Table 4a or 4b) | [7 empty] | Heat Pump | 91.3 | [%] | 0 | m3/h | 209.5386 | [%]
Efficiency adjustment factor from Table 4c [-] | [7 empty] | Complete tab HP | 1 | enter 1 if not applicable |  |  | % Renewables
Adjusted efficiency of main water heater [%] | [8 empty] | 209.5386 |  |  |  | 100% | [%] | [8 empty] | 78
Energy required for main water heater [kWh/y] | [8 empty] | 1129.1994 |  |  |  | Hot Water Demand from Heat Pump | [9 empty] | 4383.5325
Energy required for supplementary electric water heating [kWh/y] | [8 empty] | 0 |  |  |  | 2366.1086 | kWh | [8 empty] | 0
Electricity for pumps and fans and electric keep-hot facility | [6 empty] | CHP
|  |  |  | [kWh/y] |  |  | Fraction of main space and water heat from CHP |  |  |  |  | 0
Heating system |  |  |  | 52 |  |  | Heat output from CHP [kWh/y] |  |  |  |  | 0 | [10 empty] | 175
Keep-hot facility of a combi boiler |  |  |  | 0
Ventilation system |  |  |  | 48.4218
Solar water heating pump |  |  |  | 0
Electric Shower |  |  |  | 0
Total |  |  |  | 100.4218
Fuel data
|  |  | Fuel |  |  |  | Primary energy conversion factor | CO2 emission factor
[7 empty] | [-] | [kg/kWh] | [14 empty] | Prim E factors | CO2 factors
Space heating - main |  |  | electricity |  |  |  | 1.75 | 0.224 | [14 empty] | 1.1 | 0.203
Space heating - secondary |  |  | - |  |  |  | 0 | 0 | [14 empty] | 1.1 | 0.369
Water heating - main |  | 0 | electricity |  |  |  | 1.75 | 0.224 | [14 empty] | 1.1 | 0.203
Water heating - supplementary |  |  | - |  |  |  | 0 | 0 | [14 empty] | 0 | 0
Cooling |  |  | electricity |  |  |  | 1.75 | 0.224 | [6 empty] | This is populated from the Cooling tab so it can only be gas or electricity
Pumps, fans | [6 empty] | 1.75 | 0.224 | [14 empty] | 1.75 | 0.224
Energy for lighting | [6 empty] | 1.75 | 0.224 | [14 empty] | 1.75 | 0.224
Renewable and energy-saving technologies | [8 empty] | CHP Data
Type 1 | Description | [7 empty] | Heat output from CHP [kWh/y] |  |  |  | 0
| Energy produced or saved (Table 8) | [5 empty] | 1.75 | 0.224 | Electrical efficiency of CHP (e.g. 0.3) [-] |  |  |  | 0.3
| Energy consumed by the technology (Table 8) | [7 empty] | Heat efficiency of CHP (e.g. 0.5) [-] |  |  |  | 0.5
Type 2 | Description | [7 empty] | CHP fuel type |  | mains gas
| Energy produced or saved (Table 8) | [7 empty] | CHP fuel primary energy conversion factor [-] |  |  |  | 1.1
| Energy consumed by the technology (Table 8) | [7 empty] | CHP fuel CO2 emission factor [-] |  |  |  | 0.203
Type 3 | Description | [7 empty] | Energy delivered to CHP [kWh/y] |  |  |  | 0
| Energy produced or saved (Table 8) | [7 empty] | Electrical output from CHP [kWh/y] |  |  |  | 0
Energy consumed by the technology (Table 8)
Results by end use
[5 empty] | Delivered energy | Primary energy | CO2 emissions
[5 empty] | [kWh/y] | [kWh/y] | [kg/y] | [15 empty] | Deliv | Prim E | CO2 emissions
Space heating - main |  |  |  |  | 133.9636 | 234.4363 | 30.0079 | [15 empty] | 3013.2249 | 3314.5474 | 611.6847
Space heating - secondary |  |  |  |  | 0 | 0 | 0 | [15 empty] | 887.1384 | 975.8522 | 327.3541
Water heating - main |  |  |  |  | 1129.1994 | 1976.0989 | 252.9407 | [15 empty] | 4383.5325 | 4821.8858 | 889.8571
Water heating - supplementary |  |  |  |  | 0 | 0 | 0 | [15 empty] | 0 | 0 | 0
Cooling |  |  |  |  | 0 | 0 | 0 | [7 empty] | Cooling added here
Pumps, fans, electric showers |  |  |  |  | 100.4218 | 175.7382 | 22.4945 | [15 empty] | 175 | 306.25 | 39.2
Energy for lighting |  |  |  |  | 185.9537 | 325.419 | 41.6536 | [15 empty] | 698.5491 | 1222.4609 | 156.475
CHP input (individual heating systems only) |  |  |  |  | 0 | 0 | 0
CHP electrical output (individual heating system only) |  |  |  |  | 0 | 0 | 0 | [15 empty] | Total | 10640.9964 | 2024.5708
Photovoltaic/ Wind Turbine | [5 empty] | 0 | 0 | [15 empty] | per m2 | 131.3703 | 24.9947
Type 1 | Energy produced or saved |  |  |  | 0 | 0 | 0
| Energy consumed by the technology |  |  |  |  | 0 | 0
Type 2 | Energy produced or saved |  |  |  |  | 0 | 0
| Energy consumed by the technology |  |  |  |  | 0 | 0
Type 3 | Energy produced or saved |  |  |  |  | 0 | 0
| Energy consumed by the technology |  |  |  |  | 0 | 0
Energy Profile for RER calculation 2019 TGD L | [15 empty] | Conformity with Renewable Energy Technologies requirement in TGD L |  |  | 2011
|  | Electrical Delivered Energy | Thermal Delivered Energy | Biomass | Biodiesel | Bioethonal | [9 empty] | Relevant for new-build.
[8 empty] | Heat Pump |  | Heat Pump Efficiency | Heat Use | Elec Use | Environmental
Space heating - main |  | 133.9636 | 0 | 0 | 0 | 0 |  | Heat Pump as main space heating system | 1 | 398.8614 | 534.3291 | 133.9636 | 400.3655 |  |  | Renewable energy technologies in dwelling |  | Present? |  | Contribution |  | Contribution type
Space heating - secondary |  | 0 | 0 | 0 | 0 | 0 |  | Heat Pump as secondary space heating system | 0 | 0 | 0 | 0 | 0 |  |  |  |  | (yes=1, no=0) |  | [kWh/y] | [kWh/m2 y] | (thermal=1, electrical=2)
Water heating - main |  | 1129.1994 | 0 | 0 | 0 | 0 |  | Heat Pump as main water heating system | 1 | 276.9547 | 1935.907 | 698.9978 | 1236.9092 |  |  | Solar water heating system |  | 0 |  | 0 | 0 | 1
Water heating - supplementary |  | 0 | 0 | [12 empty] | Heat pump as main space heating system |  | 1 |  | 199.4201 | 2.462 | 1
Cooling |  | 0 | 0
Pumps, fans |  | 100.4218 | 0 |  |  |  |  | Renewable Electricity |  |  | Renewable Electricity |  |  |  |  | Heat pump as secondary space heating system |  | 0 |  | 0 | 0 | 1
Energy for lighting |  | 185.9537 | 0 |  |  |  |  | PV/ Wind | 0 |  | CHP | 0 |  |  |  | Heat pump as main water heating system |  | 0 |  | 0 | 0 | 1
CHP Thermal |  |  | 0 | 0 | 0 | 0 | [9 empty] | Wood/biomass/biodiesel/bioethanol heater as main space heating system |  | 0 |  | 0 | 0 | 1
[8 empty] | Renewable Other |  |  | CHP Saved |  |  |  |  | Wood/biomass/biodiesel/bioethanol heater as secondary space heating system |  | 0 |  | 0 | 0 | 1
Energy Use within Dwelling |  | 1549.5385 | 0 | 0 | 0 | 0 |  | Other | 0 |  | 0 |  |  |  |  | Wood/biomass/biodiesel/bioethanol heater as main water heating system |  | 0 |  | 0 | 0 | 1
[16 empty] | Contribution from CHP |  | 0 |  | 0 | 0 | 1
Fuel lists | [15 empty] | "Appendix Q" Renewable and Energy Saving Technologies |  | Category |  | Contribution [kWh/y]
Main | [15 empty] | Type 1 | - | Not applicable |  |  | 0 | 0
- | [15 empty] | Type 2 | - | Not applicable |  |  | 0 | 0
mains gas | [15 empty] | Type 3 | - | Not applicable |  |  | 0 | 0
bulk LPG (propane or butane)
bottled LPG | [16 empty] | Total thermal |  |  |  | 2.462
heating oil | [16 empty] | Total electrical |  |  |  | 0
house coal | [16 empty] | Overall total expressed as equivalent thermal |  |  |  | 2.462
anthracite | [16 empty] | Compliance |  |  |  | Does not comply
manufactured smokeless fuel
peat briquettes
sod peat
wood logs
wood pellets - in bags, for sec. htg
wood pellets - bulk supply, for main htg
wood chips
solid multi-fuel
electricity
Biodiesel from renewable sources only
Bioethanol from renewable sources only
YesNo
Yes | 1
No | 0
REST
Not applicable |  | 0
Renewable thermal |  | 1
Renewable electrical |  | 2
CHP
Total heat demand main space heating [kWh/y] |  |  |  |  | 534.3291
Contribution from CHP |  |  |  |  | 0
Note on A4: For micro-CHP enter thermal efficiency
Note on B41: Enter factors for fuel displaced.
Note on J41: Electrical and heat gross efficiencies may be determined from overall efficiency and heat-to-power ratio.User test data to relevant standards
Note on B42: Enter factors for fuel used by the technology.
Note on J42: Electrical and heat gross efficiencies may be determined from overall efficiency and heat-to-power ratio.User test data to relevant standards
Note on A63: Renewable and energy saving technologies 1,2,3
Note on W86: Select 'Not applicable' for energy-saving technologies that do not utilize renewable energy.
Note on Z86: Leave blank if not applicable.

## ER2
Energy requirements - group/community heating scheme | [13 empty] | Notes for DEAP SW and guidance development
This section should be used when space heating is provided by group/community heating only, with or without CHP or heat recovered from power stations.
Space heating
Secondary system
Fraction of heat use from secondary / supplementary system (from Table 7, Table 10 or Appendix F) | [9 empty] | 0
Efficiency of secondary / supplementary system [%] (from Table 4a or Appendix E) | [9 empty] | 0
Energy required for secondary space heating [kWh/y] | [9 empty] | 0
Main (group heating) system
Is charging based on heat consumed? | [5 empty] | Yes | 1
Efficiency factor for charging method [-] | [6 empty] | 1
Heat for space heating delivered to dwelling [kWh/y] | [6 empty] | 534.3291
Calculation of primary energy and CO2 emission factors
Distribution loss factor [-] (Table 9) | [6 empty] | 0
Fraction of heat from CHP unit or fraction of heat recoverd from power station | [6 empty] | 0 | From operational records or the plant design
[8 empty] | specifiaction. Enter 0 if no CHP. | [6 empty] | Heat Pump Present |  |  | Heat Pump Present
Boilers | [14 empty] | TRUE |  |  | TRUE
If the fraction of heat from boilers is zero, this section is irrelevant. | [9 empty] | Primary | CO2 |  |  |  | Airflow Volume |  |  | Airflow Volume
[9 empty] | Percent | energy | emission |  |  |  | 0 | m3/h |  | 0 | m3/h
Heat source type |  | Fuel |  |  |  |  | Efficiency |  | of heat | factor | factor |  |  |  | Efficiency of Heat Pump |  |  | Efficiency of Heat Pump
[7 empty] | [%] |  | [%] | [-] | [kg/kWh] |  |  |  | 398.8614 | [%] |  | 209.5386 | [%]
Central Boiler |  | mains gas |  |  |  |  | 0 |  | 0 | 1.1 | 0.203 | 0 | 0 |  | % Renewables |  |  | % Efficiency
Central Boiler |  | wood pellets - bulk supply, for main htg |  |  |  |  | 0 |  | 0 | 1.1 | 0.025 | 0 | 0 |  | 100% | [%] |  | 100% | [%]
Heat Pump |  | electricity |  |  |  |  | 0 | Space Heating | 0 | 1.75 | 0.224 | 0 | 0 |  | Space Heating Demand from Heat Pump |  |  | Hot Water Demand from Heat Pump
Heat Pump |  | electricity |  |  |  |  | 0 | Water Heating | 0 | 1.75 | 0.224 | 0 | 0 |  | 0 | kWh |  | 0 | kWh
Solar heating system
[8 empty] | Check total: | 0 | OK
Factors for heat delivered to dwelling from boilers | [9 empty] | 0 | 0
CHP or District Heating
If the fraction of heat from CHP/District Heating is zero, this section is irrelevant.
System type | [5 empty] | District Heating |  |  | 2 | See Appendix C2 for definitions
If CHP
| Electrical efficiency of CHP unit (e.g. 0.3) from operational records or the CHP design specification [-] | [9 empty] | 0
| Heat efficiency of CHP unit (e.g. 0.5) from operational records or the CHP design specification [-] | [9 empty] | 0
| Fuel type |  |  |  |  | mains gas
[10 empty] | Primary energy factor | CO2 emission factor
[10 empty] | [-] | [kg/kWh]
| Factors for the CHP fuel | [8 empty] | 1.1 | 0.203
| Factors for electricity displaced from grid | [8 empty] | 1.75 | 0.224
| Factors for heat leaving CHP plant | [8 empty] | 0 | 0
If District Heating | [8 empty] | Renewable Primary Energy Factor | Non Renewable Primary Energy Factor | CO2 emission factor
| Factors for District Heating | [7 empty] | 0 | 0 | 0
End if
Factors for heat delivered to dwelling from CHP/District Heating | [9 empty] | 0 | 0
Factors for heat delivered to dwelling from community heating scheme | [9 empty] | 0 | 0
Electricity for pumps and fans (mechanical ventilation only) [kWh/y] | [6 empty] | 77.4262
Fuel data
|  |  | Fuel |  |  |  | Primary energy conversion factor | CO2 emission factor
[7 empty] | [-] | [kg/kWh]
Space heating - main |  |  | group heating scheme |  |  |  | 0 | 0
Space heating - secondary |  |  | - |  |  |  | 0 | 0
Water heating main |  |  | group heating scheme |  |  |  | 0 | 0
Water heating - supplementary |  |  | not applicable |  |  |  | 0 | 0
Cooling |  |  | electricity |  |  |  | 1.75 | 0.224 | [5 empty] | Cooling added here
Pumps, fans | [6 empty] | 1.75 | 0.224
Energy for lighting | [6 empty] | 1.75 | 0.224
Renewable and energy-saving technologies
Type 1 | Description
Energy produced or saved (Table 8)
Energy consumed by the technology (Table 8)
Type 2 | Description
Energy produced or saved (Table 8)
Energy consumed by the technology (Table 8)
Type 3 | Description
Energy produced or saved (Table 8)
Energy consumed by the technology (Table 8)
Results by end use
|  |  |  | Delivered energy | Primary energy | CO2 emissions
|  |  |  | [kWh/y] | [kWh/y] | [kg/y]
Space heating - main |  |  |  | 534.3291 | 0 | 0
Space heating - secondary |  |  |  | 0 | 0 | 0
Water heating - main |  |  |  | 2366.1086 | 0 | 0
Water heating - supplementary |  |  |  | 0 | 0 | 0
Cooling |  |  |  | 0 | 0 | 0 | [7 empty] | Cooling added here
Pumps, fans, electric showers |  |  |  | 77.4262 | 135.4958 | 17.3435
Energy for lighting |  |  |  | 185.9537 | 325.419 | 41.6536
Photovoltaic/ Wind Turbine |  |  |  | 0 | 0 | 0
Type 1 | Energy produced or saved |  |  |  | 0 | 0
| Energy consumed by the technology |  |  |  | 0 | 0
Type 2 | Energy produced or saved |  |  |  | 0 | 0
| Energy consumed by the technology |  |  |  | 0 | 0
Type 3 | Energy produced or saved |  |  |  | 0 | 0
| Energy consumed by the technology |  |  |  | 0 | 0
Relevant for new-build.
Delivered energy from heat-only sources [kWh/y] |  |  |  |  | 0
Heat delivered to dwelling from CHP [kWh/y] |  |  |  |  | 0
Heat delivered to dwelling from District Heating [kWh/y] |  |  |  |  | 0
Renewable energy technologies associated with dwelling
Energy Profile for RER calculation 2019 TGD L | [15 empty] | Conformity with Renewable Energy Technologies requirement in TGD L (Section 1.2)
|  | Electrical Delivered Energy | Thermal Delivered Energy | Biomass | Biodiesel | Bioethonal | [9 empty] | Renewable Energy Technologies (TGD L Section 1.2)
[8 empty] | Heat Pump |  | Heat Pump Efficiency | Heat Use | Elec Use | Environmental |  |  | Relevant for new-build.
Group heating - Boiler type 1 |  | 0 | 0 | 0 | 0 | 0 |  | Heat Pump as main space heating system | 1 | 398.8614 | 0 | 0 | 0
Group heating - Boiler type 2 |  | 0 | 0 | 0 | 0 | 0 |  | Heat Pump as water heating system | 1 | 276.9547 | 0 | 0 | 0 |  |  | Delivered energy from heat-only sources [kWh/y] |  |  |  | 0
Group heating - System 3 |  | 0 | 0 | 0 | 0 | 0 | [9 empty] | Heat delivered to dwelling from CHP [kWh/y] |  |  |  | 0
Group heating - System 4 |  | 0 | 0 | 0 | 0 | 0 | [9 empty] | Renewable energy technologies associated with dwelling
Group heating - Solar heating system |  |  | 0 |  |  |  |  | Renewable Electricity |  |  | Renewable Electricity
Space heating - secondary |  | 0 | 0 | 0 | 0 | 0 |  | PV/ Wind | 0 |  | CHP | 0 | [8 empty] | Present? | Contribution |  | Contribution type
Cooling |  | 0 | 0
Contribution from CHP |  |  | 0 | 0 | 0 | 0 | [14 empty] | (yes=1, no=0) | [kWh/y] | [kWh/m2 y] | (thermal=1, electrical=2)
Contribution from District Heating |  |  | 0 |  |  |  |  | Renewable Other |  |  | CHP Saved |  |  |  |  | Group heating - Boiler type 1 |  |  |  |  | 0 | 0 | 0 | 1
Pumps, fans |  | 77.4262 | 0 |  |  |  |  | Other | 0 |  | 0 |  |  |  |  | Group heating - Heat pump |  |  |  |  | 0 | 0 | 0 | 1
Energy for lighting |  | 185.9537 | 0 | [12 empty] | Group heating - Heat pump |  |  |  |  | 0 | 0 | 0 | 1
Energy Use within Dwelling |  | 263.3799 | 0 | 0 | 0 | 0 | [9 empty] | Group heating - Solar heating system |  |  |  |  | 0 | 0 | 0 | 1
[16 empty] | Wood/biomass/bioethanol/biodiesel heater as secondary space heating system |  |  |  |  | 0 | 0 | 0 | 1
Tables | [15 empty] | Heat pump as secondary space heating system |  |  |  |  | 0 | 0 | 0 | 1
Fuel lists (referencing Ener1 sheet) | [15 empty] | Individual solar water heating system |  |  |  |  | 0 | 0 | 0 | 1
Group heating boilers and CHP plant |  |  |  | Individual heater | [11 empty] | Contribution from CHP |  |  |  |  | 0 | 0 | 0 | 1
- |  |  |  | - | [11 empty] | "Appendix Q" Renewable and Energy Saving Technologies |  |  |  |  | Category | Contribution [kWh/y]
mains gas |  |  |  | mains gas | [11 empty] | Type 1 | - |  |  |  | Not applicable |  | 0 | 0
bulk LPG (propane or butane) |  |  |  | bulk LPG (propane or butane) | [11 empty] | Type 2 | - |  |  |  | Not applicable |  | 0 | 0
heating oil |  |  |  | bottled LPG | [11 empty] | Type 3 | - |  |  |  | Not applicable |  | 0 | 0
house coal |  |  |  | heating oil
anthracite |  |  |  | house coal | [12 empty] | Total thermal | [5 empty] | 0
manufactured smokeless fuel |  |  |  | anthracite | [12 empty] | Total electrical | [5 empty] | 0
peat briquettes |  |  |  | manufactured smokeless fuel | [12 empty] | Overall total expressed as equivalent thermal | [5 empty] | 0
sod peat |  |  |  | peat briquettes | [12 empty] | Compliance | [5 empty] | Does not comply
wood logs |  |  |  | sod peat
wood pellets - bulk supply, for main htg |  |  |  | wood logs
wood chips |  |  |  | wood pellets - in bags, for sec. htg
solid multi-fuel |  |  |  | wood pellets - bulk supply, for main htg
waste combustion |  |  |  | wood chips
biomass or biogas |  |  |  | solid multi-fuel
electricity |  |  |  | electricity
Biodiesel from renewable sources only |  |  |  | Biodiesel from renewable sources only
Bioethanol from renewable sources only |  |  |  | Bioethanol from renewable sources only
YesNo
Yes | 1
No | 0
- | 0
System type
CHP |  |  | 1
District Heating |  |  | 2
- |  |  | 2
REST
Not applicable |  | 0
Renewable thermal |  | 1
Renewable electrical |  | 2
CHP
Contribution from CHP |  |  | 0
Note on A11: Select 'No' for flat rate charging.
Note on A13: Emission and primary energy factors and fuel cost below relate to this delivered heat.
Note on A17: The remainding fraction of heat will come from boilers.
Note on A19: This "Boilers" section covers all heat-only generators, including heat pumps and solar heating systems.
Note on J21: Annual proportion of heat output from plant met by each heat source.
Note on A22: Leave rows blank if inapplicable.
Note on H22: Default efficiency for boilers = 75%. Use manufacturer's declared efficiency in preference if known.
Note on J22: If operational records for system covering at least a year are available, take proportions from these, otherwise take proportions from boilers and heat pump from system design.
Note on J23: Ensure that total adds up to 100%.
Note on H26: For Heat Pump or Exhaust Air Heat Pump this efficiency is overwritten by efficiency in HP tab.
Note on H27: For Heat Pump or Exhaust Air Heat Pump this efficiency is overwritten by efficiency in HP tab.
Note on J28: If operational records covering at least a year are not available, calculate solar proportion using the "Appendix Q" procedure.
Note on A33: See Appendix 2 for definitions.
Note on B35: Electrical and heat efficiencies may be determined from overall efficiency and heat-to-power ratio.
Note on B42: Note in some cases these factors can be negative.
Note on A52: Note: factors apply to heat delivered to dwelling (as opposed to fuel supplied to group heating plant).
Note on B64: Enter factors for fuel displaced.
Note on B65: Enter factors for fuel used by the technology.
Note on E79: With group heating, no supplementary electric heating should be specified on 'Wh' sheet.
Note on W120: Select 'Not applicable' for energy-saving technologies that do not utilize renewable energy.
Note on Z120: Leave blank if not applicable.

## Fuel
Table 8: Fuel data
| Fuel | Primary energy factor | CO2 emission factor | Is fuel renewable (Biomass) for Part L? (1=yes; 0=no) | Is fuel renewable (Biodiesel) for Part L? (1=yes; 0=no) | Is fuel renewable (Bioethanol) for Part L? (1=yes; 0=no)
|  | [-] | [kg/kWh]
Gas | mains gas | 1.1 | 0.203 | 0 | 0 | 0
| bulk LPG (propane or butane) | 1.1 | 0.232 | 0 | 0 | 0
| bottled LPG | 1.1 | 0.232 | 0 | 0 | 0
Oil | heating oil | 1.1 | 0.272 | 0 | 0 | 0
Solid fuel | house coal | 1.1 | 0.361 | 0 | 0 | 0
| anthracite | 1.1 | 0.361 | 0 | 0 | 0
| manufactured smokeless fuel | 1.2 | 0.392 | 0 | 0 | 0
| peat briquettes | 1.1 | 0.377 | 0 | 0 | 0
| sod peat | 1.1 | 0.375 | 0 | 0 | 0
| wood logs | 1.1 | 0.025 | 1 | 0 | 0
| wood pellets - in bags, for sec. htg | 1.1 | 0.025 | 1 | 0 | 0
| wood pellets - bulk supply, for main htg | 1.1 | 0.025 | 1 | 0 | 0
| wood chips | 1.1 | 0.025 | 1 | 0 | 0
| solid multi-fuel | 1.1 | 0.369 | 0 | 0 | 0
Electricity | electricity | 1.75 | 0.224 | 0 | 0 | 0
| electricity sold to or displaced from grid | 1.75 | 0.224 | 0 | 0 | 0
Group heating | waste combustion | 1.1 | 0.057 | 0 | 0 | 0
| biomass or biogas | 1.1 | 0.025 | 1 | 0 | 0
| waste heat from power stations | 1.05 | 0.018 | 0 | 0 | 0
| - | 0 | 0 | 0 | 0 | 0
2011 biofuels added | Biodiesel from renewable sources only | 1.3 | 0.047 | 0 | 1 | 0
| Bioethanol from renewable sources only | 1.34 | 0.064 | 0 | 0 | 1
| Configurable Electricity Factors | 1.75 | 0.224

## Result
Results | [6 empty] | Notes for DEAP SW and guidance development
|  |  | Delivered energy | Primary energy | CO2 emissions
|  |  | [kWh/y] | [kWh/y] | [kg/y]
Space heating - main |  |  | 133.9636 | 234.4363 | 30.0079
Space heating - secondary |  |  | 0 | 0 | 0
Water heating - main |  |  | 1129.1994 | 1976.0989 | 252.9407
Water heating - supplementary |  |  | 0 | 0 | 0
Cooling |  |  | 0 | 0 | 0 |  | Cooling added here
Pumps, fans, etc. |  |  | 100.4218 | 175.7382 | 22.4945
Energy for lighting |  |  | 185.9537 | 325.419 | 41.6536
CHP input (individual heating systems only) |  |  | 0 | 0 | 0
CHP electrical output (individual heating system only) |  |  | 0 | 0 | 0
Photovoltaic/ Wind Turbine |  |  | 0 | 0 | 0
Type 1 |  |  | 0 | 0 | 0
Type 2 | - |  | 0 | 0 | 0
Type 3 | - |  | 0 | 0 | 0
Total |  |  | 1549.5385 | 2711.6924 | 347.0966
per m2 floor area |  |  | 19.1301 | 33.4777 | 4.2851
[kWh/m2 y]
Building Energy Rating |  |  |  | 33.4777 | A2
Results from IEQ tab displayed here
Check conformity with MPEPC, MPCPC and RER requirements in TGD L
Relevant for new-build.
|  |  | Primary energy |  | CO2 emissions | Renewable
|  |  | [kWh/y] |  | [kg/y] | Energy Ratio
Totals for reference dwelling |  |  | 10640.9964 |  | 2024.5708
|  |  | EPC |  | CPC | RER
Performance coefficients |  |  | 0.25483 |  | 0.17144 | 0.37647
Maximum permitted |  |  | 0.3 |  | 0.35 | 0.2
|  |  | Complies |  | Complies | Complies
Subsidiary processing
|  |  | Prim E |  | CO2
Error value in reference dwelling result? |  |  | FALSE |  | FALSE
Lists
BER
Bound | Lower limit | Label
-1000 | -1000 | A1
25 | 25 | A2
50 | 50 | A3
75 | 75 | B1
100 | 100 | B2
125 | 125 | B3
150 | 150 | C1
175 | 175 | C2
200 | 200 | C3
225 | 225 | D1
260 | 260 | D2
300 | 300 | E1
340 | 340 | E2
380 | 380 | F
450 | 450 | G
Note on A14: Renewable and energy saving technologies 1,2,3
Note on A20: A BER certificate can be provided only by a registered BER assessor.

## RER
| Electrical Delivered Energy | Thermal Delivered Energy | Biomass | Biodiesel | Bioethonal | Heat Pump Environmental | Generated Electricity | Generated Electricity CHP | Other Renewable | District | CHP Energy Saved
Energy Use within Dwelling | 1549.5385 | 0 | 0 | 0 | 0 | 1637.2747 | 0 | 0 | 0 | 0 | 0
|  | E | fPnren | fPren on-site | EPnren | Epren on-site | EPtot | RER
|  | kWh |  |  | kWh | kWh | kWh | nrb-os
+ Delivered energy | PV/Wind | 0 | 0 | 1.75 | 0 | 0 | 0
+ Delivered energy | Other | 0 | 0 | 1 | 0 | 0 | 0
+ Delivered energy | Solar | 0 | 0 | 1 | 0 | 0 | 0
+ Delivered energy | Biomass | 0 | 0.1 | 1 | 0 | 0 | 0
+ Delivered energy | Biodiesel | 0 | 0.3 | 1 | 0 | 0 | 0
+ Delivered energy | Bioethanol | 0 | 0.34 | 1 | 0 | 0 | 0
+ Environmental energy | HP | 1637.2747 | 0 | 1 | 0 | 1637.2747 | 1637.2747
+ Saved energy | CHP | 0 | 0 | 1 | 0 | 0
+ Delivered energy | District Heating | 0 | 0 | 0 | 0 | 0 | 0
+ Delivered energy | Grid | 1549.5385 | 1.75 | 0 | 2711.6924 | 0 | 2711.6924
+ Delivered energy | Thermal | 0 | 1.1 | 0 | 0 | 0 | 0
TOTAL STEP A |  |  |  |  | 2711.6924 | 1637.2747 | 4348.9671 | 0.37647 | RER for use in Building Regulation Compliance
- Energy not used in Regulated Loads | PV/Wind/CHP | 0 | 1.75 | 0 | 0 | 0 | 0
Excluding Energy not used in Regulated Loads |  |  |  |  | 2711.6924 | 1637.2747 | 4348.9671 | 0.37647 | RER without Energy not Used in Regulated Load.

## SWH
Solar water heating
Calculation of solar input (from Appendix H) | [5 empty] | DEAP manual reference
Aperture area of solar collector [m2 ] |  |  |  | 0 |  | [H1]
if only the gross area can be established reliably, multiply it by ratio in Table H1
Zero-loss collector efficiency, η0, from test certificate or Table H1 [-] |  |  |  | 0 |  | [H2]
Collector heat loss coefficient, a1 [W/m2 K], from test certificate or Table H1 |  |  |  | 0 |  | [H3]
Collector performance ratio, a1/η0 [W/m2 K] |  |  |  | 0 |  | [H4]
Annual solar radiation [kWh/m2] from Table H2 |  |  |  | 0 |  | [H5]
Overshading factor [-] from Table H3 |  |  |  | 0 |  | [H6]
Solar energy available [kWh/y] |  |  |  | 0 |  | [H7]
Solar-to-load ratio [-] |  |  |  | 0 |  | [H8]
Utilisation factor [-] |  |  |  | 0 |  | [H9]
| If the cylinder is heated by a boiler, is there a cylinder stat? | Yes |  | 1
| Adjusted utilisation factor [-] |  |  | 0
Collector performance factor |  |  |  | 0.87 |  | [H10]
Dedicated solar storage volume, Vs [litres] |  |  |  | 0 |  | [H11]
Volume of pre-heat store, or dedicated solar volume of a combined cylinder
Is solar storage contained within a combined cylinder? |  |  | Yes | 1
| If yes, total volume of cylinder [litres] |  |  | 180 | - | [H12]
Effective solar volume, Veff [litres] |  |  |  | 54 |  | [H13]
Daily hot water usage, Vd [litres] |  |  |  | 111.9566 |  | [H14]
Volume ratio, Veff/Vd [-] |  |  |  | 0.48233 |  | [H15]
Solar storage volume factor, f(Veff/Vd) |  |  |  | 0.85417 |  | [H16]
Solar DHW input, Qs [kWh/y] |  |  |  | 0 |  | H17]
Notes:
1. Some formulae above reference the 'Wh' worksheet.
2. Reference the result - the solar DHW input, Qs - from the 'Wh' sheet where applicable.
List
- | 0
Yes | 1
No | 0
Not applicable | 1

## Summer
Assessment of internal temperature in summer
from Appendix P
This worksheet does not form part of the DEAP rating calculation; it is provided for information only.
Dwelling volume [m3] |  | 198.45
Effective air change rate for summer period [ac/h] (Table P1) |  | 0.8
Ventilation heat loss coefficient [W/K] |  | 52.3908
Fabric heat loss coefficient [W/K] |  | 28.2383
Heat loss coefficient under summer conditions, H [W/K] |  | 80.6291
Total solar gains for summer period [W/m2] |  | 632.9353
Internal gains [W] |  | 415.8782
Total gains in summer [W] |  | 1048.8135
Temperature increment due to gains [C] |  | 13.0079
Summer mean external temperature [C] (Table P2) |  | 15 | default 15
Heat capacity parameter [MJ/m2 K] |  | 0.2
(Internal heat capacity of dwelling (24 hr) divided by its total floor area)
Temperature increment related to thermal mass [C] |  | 0.6
Threshold internal temperature [C] |  | 28.6079
Table 1c: Solar flux for summer period [W/m2]
North | 78
NE/NW | 93
East/West | 111
SE/SW | 115
South | 110
Horizontal | 185

## HP
Assessment of Heat Pump Performance | [6 empty] | I.S. EN 14825 | Yes | Space heating | Air to Water | Heat Emission Type | Fuel |  | Fixed Outlet | Yes | NA | No Hot Water Store | 3XS | ERROR | 0 | 8 | Water heating energy efficiency, ηwh
Description: | Value: | Unit: | Guidance Notes: |  |  |  | I.S. EN 14511 | No | Same Heat Pump providing Space Heating and Domestic Hot Water | Brine to Water | 1 or more Radiators present | Electricity | 1.75 | Variable Outlet | No | Low Temperature | Integral Hot Water Storage | XXS |  | 0 | 16 | Coefficient of Performance, COP
Total heat loss (W/K) taken from DEAP | 60.9825 | W/K | Source from the Building Elements - Heat Loss Results Tab in DEAP |  |  |  | I.S. EN 255-3 |  | Separate Heat Pump providing Space Heating and Domestic Hot Water | Water to Water | Fan Coil Units present (no radiators) | Mains Gas | 1.1 |  |  | High Temperature | Separate Hot Water Storage | XS |  | 0 | 24
Heat Loss Watts | 1372.1067 | Watts | Required Heating Capacity at design conditions. |  |  |  | I.S. EN 16147 |  |  | Exhaust Air to Water | Underfloor heating only | LPG Gas (bottled or bulk) | 1.1 |  |  | Very High Temperature | Integral and separate Hot Water Storage | S
Is the Heat Pump part of a Group Heating Scheme | No | [8 empty] | Air to Air | Air | Heating Oil | 1.1 |  |  |  |  | M
Proportion of group heating provided by the heat pump | 0% | % | [7 empty] | Brine to Air |  | Biodiesel from renewable sources only | 1.3 |  |  |  |  | L
Floor Area of Dwelling | 0 | m2 | Source from DEAP | [6 empty] | Water to Air |  | Bioethanol from renewable sources only | 1.34 |  |  |  |  | XL
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 81 | m2 | [9 empty] | House coal/ Anthracite | 1.1 |  |  |  |  | XXL
Heat Pump for Space Heating | [6 empty] | Code for Space Heating/ DHW |  |  |  |  | manufactured smokeless fuel | 1.2 |  |  |  |  | 3XL
Manufacturer of the installed heat pump(s) |  |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology |  |  |  | TRUE | Space Heating served by HP |  |  |  | Peat | 1.1 |  |  |  |  | 4XL
Model of the installed heat pump(s) |  |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology |  |  |  | TRUE | Hot Water served by HP |  |  |  | Wood logs/pellets/chips | 1.1
Type of heat pump | Air to Water |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology |  |  |  | FALSE | Same HP for Space and Water Heating |  |  |  | Solid multi-fuel | 1.1
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Variable Outlet |  | Source from Ecodesign Data
Space Heating Test Standard | I.S. EN 14825 |  | Source from Ecodesign Data or HARP Database
Operation Limit Temperature (TOL) | -10 | oC | Source from Ecodesign Data
Heating water operating limit temperature (WTOL) | 55 | oC | Source from Ecodesign Data
Annual space heating provided by Heat Pump | 534.3291 | kWh
Design Outdoor Temperature | -3 | oC | Based on CIBSE Guide A Section 2
Indoor Design Temperature (Mean Internal Temperature) | 19.5 | oC | Source from Net Space Heat Demand "Required mean internal temperature during heating hours degC"
Heat emission type served by heat pump within the dwelling: | Select all that apply:
1 or more Radiators | Yes
1 or more Fan Coil Units | No |  | Default Supply Temperature
Underfloor Heating | No |  | 55 | oC | Based on SAP input parameters.
Air used as Emitter (to Air Units) | No
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 50 | oC | WARNING: As Design Flow Temperature is less than Default, please ensure that documentary evidence is available to support it |  |  |  |  | Note: have deleted Row 31 as this is dealt with in the calcs on heating calc (row 38)
Exponent n, characterising type of emission system | 1.2 |  | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Emitter Temperature Drop | 10 | oC | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Return Temperature at design conditions | 40
No of Hrs per Day Heat Pump in Operation | 24 | hrs | Source from Designer/ Installer sign off sheet, default is DEAP heating schedule which is 8 hrs a day
Cut-out hours | 0
Electricity Primary Energy Factor | 1.75 |  | Source from DEAP tool, Options
Is a Back Up Space Heater Present within Dwelling | No |  | Source from Designer/ Installer sign off sheet
Back Up Space Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Space Heater | 1.75
Efficiency of Back up Space Heater | 100% | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Space Heater relative to Direct Electric Heating | 1
Test Conditions I.S. EN 14825 | Medium Temperature data is mandatory requirement under Ecodesign Directive (Note this was referred as High Temperature in earlier versions of EN 14825) |  | Source from Ecodesign Data or accredited tests to EN14825
Additional Test Points available at: | Low Temperature | Yes | Source from Ecodesign Data or accredited tests to EN14825
| Intermediate Temperature | No | Source from Ecodesign Data or accredited tests to EN14825
| High Temperature | No | Source from Ecodesign Data or accredited tests to EN14825
| Maximum Test Temperature allowed for in EN14825 testing | 55
| Test Conditions I.S. EN 14825 | A (88%) -7oC | B (54%) 2oC | C (35%) 7oC | D (15%) 12oC | E* (100%) TOL
Low Temperature Application (35oC) | Source | A-7 | A2 | A7 | A12 | A-10
Source from Ecodesign data or I.S. EN14825 Table 8 for air source. Table 12 for brine or water source. [These table # references are from 2016 version of this standard] | Sink | W34 | W30 | W27 | W24 | W35
| Heating Capacity (kW) | 3.39 | 2.08 | 1.35 | 1.43 | 3.05
| Coefficient of Performance (kW/kW) | 2.63 | 3.5 | 4.3 | 4.7 | 2.6
Intermediate Temperature Application (45oC) | Source | A-7 | A2 | A7 | A12 | A-10
Source from Ecodesign data or I.S. EN14825 Table 9 for air source. Table 13 for brine or water source. [These table # references are from 2016 version of this standard] | Sink | W43 | W37 | W33 | W28 | W45
| Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0
| Coefficient of Performance (kW/kW) | 0 | 0 | 0 | 0 | 0
Medium Temperature Application (55oC) | Source | A-7 | A2 | A7 | A12 | A-10
Source from Ecodesign data or I.S. EN14825 Table 10 for air source. Table 14 for brine or water source. [These table # references are from 2016 version of this standard] | Sink | W52 | W42 | W36 | W30 | W55
| Heating Capacity (kW) | 3.4 | 2.08 | 1.35 | 1.43 | 3.05
| Coefficient of Performance (kW/kW) | 2.2 | 3.13 | 4 | 4.6 | 2.05
High Temperature Application (65oC) | Source | A-7 | A2 | A7 | A12 | A-10
Source from Ecodesign data or I.S. EN14825 Table 11 for air source. Table 15 for brine or water source. [These table # references are from 2016 version of this standard] | Sink | W61 | W49 | W41 | W32 | W65
| Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0
| Coefficient of Performance (kW/kW) | 0 | 0 | 0 | 0 | 0
Heat Pump for Water Heating
Manufacturer of the installed heat pump(s) |  |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology
Model of the installed heat pump(s) |  |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology | [8 empty] | manufactured smokeless fuel | 1.2 |  |  |  |  | 3XL
Type of heat pump | Air to Water |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology | [8 empty] | Peat | 1.1 |  |  |  |  | 4XL
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Variable Outlet |  | Source from Ecodesign Data | [8 empty] | Wood logs/pellets/chips | 1.1
Describe the water heating heat pump arrangement | Separate Heat Pump providing Space Heating and Domestic Hot Water |  | Source from Designer/ Installer sign off sheet or site evidence without Ecodesign | [8 empty] | Solid multi-fuel | 1.1
Water Heating Test Standard | I.S. EN 16147 |  | Source from Ecodesign Data or HARP Database
Output from Main Water Heater | 2366.1086 | kWh/yr | Source from the Water Heating Tab, Output from Main Water Heater in DEAP
Type of DHW | Separate Hot Water Storage |  | An Integral Hot Water Store forms part of the Heat Pump, refer to DEAP Heat Pump Methodology for guidance.
Cold Water Inlet Temperature | 10 | oC | Based on DEAP Methodology
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | oC | Based on DEAP Methodology and guidelines for prevention of Legionella. Where the store is separate to the heat pump a 5oC drop is assumed.
Volume of DHW Storage | 180 | litres | Source from the Water Heating Tab, Storage in DEAP
Is there a water heater installed as back up for the heat pump | No |  | Source from Designer/ Installer sign off sheet
Back Up Water Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Water Heater | 1.75
Efficiency of Back up Water Heater | 100% | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Water Heater relative to Direct Electric Heating | 1
Test Conditions EN 16147
Source of data | Water heating energy efficiency, ηwh |  | Source from Ecodesign Data or accredited tests to EN 16147
Water heating energy efficiency, ηwh | 96 | % | Source from Ecodesign Data or accredited tests to EN 16147
Equivalent Coefficient of Performance | 2.4 | kW/kW
Reference Hot Water Temperature | 55 | oC | Source from Ecodesign Data or accredited tests to EN 16147, set at 40oC if unknown.
Required Source Temperature | 7 | oC | Based on Table 5 of EN 16147
Hot water Rated Heat output Prated | 1.35 | kW | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147
Declared Load Profile | M |  | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147
Standing heat loss of test storage tank | 0.9 | kWh/day | Source from Ecodesign Data or accredited tests to EN 16147, set as 0 if unknown
Volume of DHW accounted for in test | 120 | litre | Source from Ecodesign Data or accredited tests to EN 16147
Test Conditions EN 14511-2
Is the Heat Pump Listed on HARP | Yes
Enter SPF based on DEAP Methodology/ HARP | 3 | kW/kW | Derive SPF from HARP, certified data COPs in compliance with DEAP methodology or from DEAP table 4a defaults
Is there load or weather compensation present? | Yes |  | Source from Designer/ Installer sign off sheet or site evidence
Does the heat pump have an Integral Immersion | No |  | Source from Designer/ Installer sign off sheet or site evidence
Does heat pump reach a flow temperature of >=65oC | No |  | Source from CE marked literature, CE marked dataplates or accredited test data for the heat pump in question.
Test Conditions EN 255-3
Coefficient of Performance | 0 | kW/kW | Source from accredited test data certificate
Reference Hot Water Temperature | 0 | oC | Source from accredited test data certificate, set at 40oC if unknown.
Heating Capacity DHW | 0 | kW | Source from accredited test data certificate
Results
Results
Efficiency of Main Heating System | 398.9% | % | Enter this in DEAP: energy requirements: space heating
Efficiency Adjustment Factor - Main Heating | 1 |  | Enter this in DEAP: energy requirements: space heating
Efficiency of Main Hot Water System | 209.5% | % | Enter this in DEAP: energy requirements: water heating
Efficiency Adjustment Factor - Main Hot Water | 1 |  | Enter this in DEAP: energy requirements: water heating
% Renewable Contribution from Exhaust Heat Pump for Space Heating | NA
% Renewable Contribution from Exhaust Heat Pump for Water Heating | NA
% of Heating Provided by Heat Pump | 100% | Space Heating Provided by Heat Pump | 534.3291 | Efficiency of Space Heat Pump | 398.8614
% of Hot Water Provided by Heat Pump | 81.82% | Water Heating Provided by Heat Pump | 1935.907 | Efficiency of Water Heat Pump | 276.9547
Colour Key
User Input, only editable cells
Calculated Value
Constant
User does not need to edit,
based on previous inputs

## Heating Calc
EN 15316 methodology |  | Bin 1 | Bin 2 | Bin 3 | Bin 4 | Bin 5 | Total | Guidance Note |  |  |  | Back Up Heating |  |  |  |  | 534.3291 | 2366.1086 | [5 empty] | 0
Bin Data | I.S. EN 14825 Test Conditions | (E) 100% | (A) 88% | (B) 54% | (c) 35% | (D)15%
Operating Points (Bin Temperatures) | Test Points | -10 | -7 | 2 | 7 | 12 |  | Taken from IS EN 14825 standard |  | TOL | kW | Outdoor temperature bin (deg C) | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8 | Bin Time (h) | Effective Bin Time (h) | Energy to be produced for SH (kWh) | Energy to be produced for DHW (kWh) | Energy Required from Heat Pump (kWh) | Supply Flow Temp oC…B1 | Heating Capacity kW…As per D12 and MCS Tool* (see below) | Required Running Hours (hr) Eqt 28 | Diff between Required Running Hrs and Effective Bin..Eqt 40 | SAP Methodology Back Up Heater based on Plant Size Ratio | Energy Required from back up (kWh)…Eqt 40 | Total Back Up Heater | SAP Methodology - Table N9
Lower Limit (oC ) | Mid Test Points | -12 | -8.5 | -2.5 | 4.5 | 9.5 |  | For Bin 1, the Lower Limit is the Lowest Outdoor Temperature as per D.1.3.2.1 |  | -10 | 3.05 | -12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.2531 | 2.8157 | 0 | 0 | 0 | 0 | 0 | Plant Size Ratio | 24 | 16 | 11
Upper Limit, (oC ) | Mid Test Points | -8.5 | -2.5 | 4.5 | 9.5 | 35 |  | For Bin 5, the Upper Limit is the Upper Outdoor Temperature as per D.1.3.2.1 |  |  |  | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.1355 | 2.9328 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.53 | 0.64
Source Temperature (oC) |  | -10 | -7 | 2 | 7 | 12 | [5 empty] | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0131 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.28 | 0.43 | 0.57
Weighting Factor SH | Eqt 4 | 0 | 0.005882 | 0.30194 | 0.46292 | 0.22926 | 1 |  |  |  |  | -9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8855 | 3.1672 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.19 | 0.34 | 0.49
Space Heating Energy (kWh) | Eqt 5 | 0 | 3.1429 | 161.3346 | 247.3535 | 122.4981 | 534.3291 |  |  |  |  | -8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.7526 | 3.2843 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.12 | 0.27 | 0.42
Bin Time (h) | Eqt 6 | 0 | 18 | 1247 | 2933 | 4562 | 8760 |  |  |  |  | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.6142 | 3.4015 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.06 | 0.2 | 0.35
Effective Bin Time (h) | Eqt 7 | 0 | 18 | 1247 | 2933 | 4562 | 8760 |  |  |  |  | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.47 | 3.2546 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0.03 | 0.14 | 0.29
Weighting Factor DHW | Eqt 8 | 0 | 0.0020548 | 0.14235 | 0.33482 | 0.52078 | 1 |  |  |  |  | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.3198 | 3.1078 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.01 | 0.09 | 0.24
DHW Energy (kWh) | Eqt 9 | 0 | 4.8619 | 336.8193 | 792.2142 | 1232.2132 | 2366.1086 |  |  |  |  | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.1632 | 2.961 | 0 | 0 | 0 | 0 | 0 | 0.55 | 0 | 0.06 | 0.19
[12 empty] | -3 | 0.0013629 | 0.00045662 | 4 | 4 | 0.72824 | 1.0804 | 0.72824 | 50 | 2.8141 | 0.25878 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0.03 | 0.15
Test Data |  | -10 | -7 | 2 | 7 | 12 | [5 empty] | -2 | 0.0045191 | 0.0015982 | 14 | 14 | 2.4147 | 3.7815 | 2.4147 | 48.8298 | 2.6673 | 0.90529 | 0 | 0 | 0 | 0 | 0.65 | 0 | 0.02 | 0.11
Low Temperature (oC ) | Taken from EN 14825 test data | 35 | 34 | 30 | 27 | 24 | [5 empty] | -1 | 0.013414 | 0.0050228 | 44 | 44 | 7.1674 | 11.8846 | 7.1674 | 47.6522 | 2.5205 | 2.8437 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0.01 | 0.09
Intermediate Temperature (oC ) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0.032136 | 0.012785 | 112 | 112 | 17.1712 | 30.2516 | 17.1712 | 46.4668 | 2.3737 | 7.2341 | 0 | 0 | 0 | 0 | 0.75 | 0 | 0 | 0.05
Medium Temperature (oC ) | Taken from EN 14825 test data | 55 | 52 | 42 | 36 | 30 | [5 empty] | 1 | 0.039273 | 0.016667 | 146 | 146 | 20.9849 | 39.4351 | 20.9849 | 45.2731 | 2.2268 | 9.4237 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0.05
High Temperature (oC ) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 | [5 empty] | 2 | 0.055736 | 0.025342 | 222 | 222 | 29.7813 | 59.963 | 29.7813 | 44.0706 | 2.08 | 14.3179 | 0 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0.03
Low Temperature COP (kW/kW) | Taken from EN 14825 test data | 2.6 | 2.63 | 3.5 | 4.3 | 4.7 |  | Taken from Input Sheet Low Temperature COP |  |  |  | 3 | 0.075301 | 0.036872 | 323 | 323 | 40.2354 | 87.2435 | 40.2354 | 42.8587 | 1.934 | 20.8043 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0.02
Intermediate Temperature COP (kW/kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Intermediate Temperature COP |  |  |  | 4 | 0.086079 | 0.045662 | 400 | 400 | 45.9943 | 108.0415 | 45.9943 | 41.6368 | 1.788 | 25.7239 | 0 | 0 | 0 | 0 | 0.95 | 0 | 0 | 0.01
Medium Temperature COP (kW/kW) | Taken from EN 14825 test data | 2.05 | 2.2 | 3.13 | 4 | 4.6 |  | Taken from Input Sheet Medium Temperature COP |  |  |  | 5 | 0.087979 | 0.050913 | 446 | 446 | 47.01 | 120.4663 | 47.01 | 40.4041 | 1.642 | 28.6297 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.01
High Temperature COP (kW/kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet High Temperature COP |  |  |  | 6 | 0.097735 | 0.062215 | 545 | 545 | 52.2227 | 147.2065 | 52.2227 | 39.1597 | 1.496 | 34.9082 | 0 | 0 | 0 | 0 | 1.05 | 0 | 0 | 0
Low Temperature Heating Capacity (kW) | Taken from EN 14825 test data | 3.05 | 3.39 | 2.08 | 1.35 | 1.43 |  | Taken from Input Sheet Low Temperature Capacity |  |  |  | 7 | 0.097323 | 0.068836 | 603 | 603 | 52.0023 | 162.8725 | 52.0023 | 37.9025 | 1.35 | 38.5202 | 0 | 0 | 0 | 0
Intermediate Temperature Heating Capacity (kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Intermediate Temperature Capacity |  |  |  | 8 | 0.0944 | 0.075114 | 658 | 658 | 50.4404 | 177.7282 | 50.4404 | 36.6315 | 1.366 | 36.9256 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.014337
Medium Temperature Heating Capacity (kW) | Taken from EN 14825 test data | 3.05 | 3.4 | 2.08 | 1.35 | 1.43 |  | Taken from Input Sheet Medium Temperature Capacity |  |  |  | 9 | 0.085487 | 0.07774 | 681 | 681 | 45.6781 | 183.9406 | 45.6781 | 35.3451 | 1.382 | 33.0522 | 0 | 0 | 0 | 0
High Temperature Heating Capacity (kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet High Temperature Capacity |  |  |  | 10 | 0.068755 | 0.072945 | 639 | 639 | 36.7379 | 172.5963 | 36.7379 | 34.0417 | 1.398 | 26.2789 | 0 | 0 | 0 | 0
[12 empty] | 11 | 0.059179 | 0.075342 | 660 | 660 | 31.6211 | 178.2685 | 31.6211 | 32.7191 | 1.414 | 22.3629 | 0 | 0 | 0 | 0
Appropriate Test Data | Lower Test Points | Low | [9 empty] | 12 | 0.043757 | 0.069635 | 610 | 610 | 23.3804 | 164.7633 | 23.3804 | 31.3746 | 1.43 | 16.35 | 0 | 0 | 0 | 0
| Higher Test Points | Medium | [9 empty] | 13 | 0.031311 | 0.066438 | 582 | 582 | 16.7304 | 157.2004 | 16.7304 | 30.0049 | 1.446 | 11.5701 | 0 | 0 | 0 | 0
| To Air Heat Pump | No | [9 empty] | 14 | 0.017252 | 0.054909 | 481 | 481 | 9.218 | 129.9199 | 9.218 | 28.6052 | 1.462 | 6.3051 | 0 | 0 | 0 | 0
Lower Test Points - Temperature (oC) | Low | 35 | 34 | 30 | 27 | 24 | [5 empty] | 15 | 0.0090024 | 0.057306 | 502 | 502 | 4.8102 | 135.5921 | 4.8102 | 27.1691 | 1.478 | 3.2546 | 0 | 0 | 0 | 0
Higher Test Points - Temperature (oC ) | Medium | 55 | 52 | 42 | 36 | 30 | [5 empty] | 16 |  | 0.043721 | 383 | 383 |  | 103.4497 | 0
Lower Test Points - COP (kWh/kWh) | Low | 2.6 | 2.63 | 3.5 | 4.3 | 4.7 | [5 empty] | 17 |  | 0.029566 | 259 | 259 |  | 69.9569 | 0
Higher Test Points - COP (kWh/kWh) | Medium | 2.05 | 2.2 | 3.13 | 4 | 4.6 | [5 empty] | 18 |  | 0.019406 | 170 | 170 |  | 45.9176 | 0
Lower Test Points - Heating Capacity (kW) | Low | 3.05 | 3.39 | 2.08 | 1.35 | 1.43 | [5 empty] | 19 |  | 0.012785 | 112 | 112 |  | 30.2516 | 0
Higher Test Points - Heating Capacity (kW) | Medium | 3.05 | 3.4 | 2.08 | 1.35 | 1.43 | [5 empty] | 20 |  | 0.0076484 | 67 | 67 |  | 18.0969 | 0 |  | * Interpolation equation as per EN 15316, however using same methodology as MCS tool as single point data may ony be available
Supply Flow Temperature based on Single Test Points | Equation B1 - Based on 55oC only | 64.2793 | 60.3447 | 48.1258 | 40.9662 | 33.3762 |  | Supply Flow Temperature based on 55oC, to meet the mandatory test points in Ecodesign, to use for single test point data |  |  |  | 21 |  | 0.0042237 | 37 | 37 |  | 9.9938 | 0
Source Temperature | Section F2.1 | -10 | -7 | 2 | 7 | 12 | [5 empty] | 22 |  | 0.0030822 | 27 | 27 |  | 7.2928 | 0
Supply Flow Temperature | Equation B1 | 58.0131 | 54.6142 | 44.0706 | 37.9025 | 31.3746 | [5 empty] | 23 |  | 0.0022831 | 20 | 20 |  | 5.4021 | 0
Heating Capacity for Source Temp | Section 5.3.5.1.3 | Not applicable, for water and exhaust heat pumps the source temperature is constant, for air heat pumps we have test data at various conditions and for brine heat pumps as we don't have different source temperatures it is not possible to carry out interpolation. | [9 empty] | 24 |  | 0.001484 | 13 | 13 |  | 3.5113 | 0
Heating Capacity for Supply Temp | Linear Interpolation (5.3.5.1.3) (Eqt D12) | 3.05 | 3.4015 | 2.08 | 1.35 | 1.43 |  | Refer to Heating Capacity calculated for each external temperature as per Column W. Note: As per Annex D, heating capacity cannot be adjusted for single test points |  |  |  | 25 |  | 0 | 0 | 0 |  | 0 | 0
[12 empty] | 26 |  | 0 | 0 | 0 |  | 0 | 0
Standard Rating Conditions | Based on EN 14511 | 1.35 | kW |  |  |  |  | In EN 14825, the water flow rate is determined according to EN 14511 at standard rating conditions. |  |  |  | 27 |  | 0 | 0 | 0 |  | 0 | 0
Mass Flow Rate | kg/s, Equation 10 | 0.064562 | [5 empty] | 5K is based on EN14511 for electrically driven heat pumps, 4.182 kJ/kg/K is the specific heat capacity of water. |  |  |  | 28 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Lower Temp | oC, Equation 10 | 11.2963 | 12.5556 | 7.7037 | 5 | 5.2963 | [5 empty] | 29 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Higher Temp | oC, Equation 10 | 11.2963 | 12.5926 | 7.7037 | 5 | 5.2963 | [5 empty] | 30 |  | 0 | 0 | 0 |  | 0 | 0
Required Heating Capacity at design conditions | Taken from DEAP | 1.3721 | kW |  |  |  |  | PSR | 0.98389 |  |  | 31 |  | 0 | 0 | 0 |  | 0 | 0
Delta T for emitter | Taken from Input | 10 | [9 empty] | 32 |  | 0 | 0 | 0 |  | 0 | 0
Required Mass flow at design conditions | kg/s, Equation 10 | 0.03281 | [9 empty] | 33 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Lower Temp Test Points at design conditions | oC, Equation 10 | 22.2286 | 24.7065 | 15.1592 | 9.8389 | 10.4219 | [5 empty] | 34 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Higher Temp Test Points at design conditions | oC, Equation 10 | 22.2286 | 24.7794 | 15.1592 | 9.8389 | 10.4219 | [5 empty] | 35 |  | 0 | 0 | 0 |  | 0 | 0
Correction Factor COP Lower Temp Test Points | eqt 11 | 1.1108 | 1.1358 | 1.1092 | 1.088 | 1.1324
Correction Factor COP Higher Temp Test Points | eqt 11 | 1.0788 | 1.0972 | 1.0808 | 1.0663 | 1.1011
COP corrected for Lower Temp | eqt 11 | 2.888 | 2.9873 | 3.8821 | 4.6783 | 5.3224
COP corrected for Higher Temp | eqt 11 | 2.2116 | 2.4138 | 3.3828 | 4.2651 | 5.065
Interpolation of COP | Linear Interpolation (5.3.5.1.3), refer to Eqt D11 Single Point eqt C5/C6 | 2.1097 | 2.3305 | 3.2967 | 4.1778 | 5.006 |  | For Single set of test points, the COP is based on adjustment in Annex C and is based on Supply Temp of 55oC, to meet the mandatory test results for Ecodesign. As outlined in Annex C, accuracy deteriorates with increasing distance from test points therefore methodology not used for Fixed Outlet
Storage Losses |  | Buffer Vessels for space heating only excluded, as per other systems in DEAP
Space Heating Energy Requirement | kWh | 0 | 3.1429 | 161.3346 | 247.3535 | 122.4981 | 534.3291
Energy to be produced by back up heater for Space Heating only | kWh | 0 | 0 | 0 | 0 | 0
Energy Provided by Backup Space Heater for Space Heating Only | kWh | 0 | 0 | 0 | 0 | 0 | 0 | For non electric back up heaters this has been converted to equivalent electric energy using Bivalent system
Back Up for Temperature Increase not included as test data for higher temperatures must be provided.
Auxiliary Energy for central heating pumps & DHW pumps excluded as allowed for in DEAP
Recoverable heat from auxiliary energy (pumps) and thermal losses (storage) excluded as allowed for in DEAP
Electrical Energy for Space Heating from heat pump | kWh | 0 | 1.3486 | 48.9383 | 59.2066 | 24.4701 | 133.9636
Total Electrical Energy Required | kWh | 0 | 1.3486 | 48.9383 | 59.2066 | 24.4701 | 133.9636
SPF - Heat Pump & Back up Heater | [6 empty] | 3.9886
Renewable Contribution calculated in DEAP | [6 empty] | 199.4201 | kWh
Space Heating Provided by Heat Pump | kWh | 0 | 3.1429 | 161.3346 | 247.3535 | 122.4981 | 534.3291
SPF - Heat Pump only | [6 empty] | 3.9886
Renewable Contribution provided by Heat Pump |  | 0 | 1.7943 | 112.3962 | 188.1469 | 98.0281 | 400.3655 | kWh
% Renewable |  | 100% | 100% | 100% | 100% | 100%
Renewable Contribution from Exhaust Air Heat Pump |  | 0 | 1.7943 | 112.3962 | 188.1469 | 98.0281 | 400.3655 | kWh
[7 empty] | 100% | % renewables

## DHW Calc
From Ecodesign / 814
EN 16147 |  |  |  | Tapping Cycle | kWh/day |  | Test Check | Installed Check | Error - Test | Error - Dwelling
Volume of Tank in Test | 120 |  | based on test data | 3XS | 0.345 | 7 |  |  | 0 | 0
Average Storage Temperature | 65 | oC |  | XXS | 2.1 | 15 |  |  | 0 | 0
Standby Heat loss | 0.9 | kWh/day | based on test data | XS | 2.1 | 15 |  |  | 0 | 0
Declared Load Profile | M |  |  | S | 2.1 | 36 |  |  | 0 | 0
Min Volume for cycle | 65 | litre |  | M | 5.845 | 65 | 43.3333 | 39 | 0 | 0
DHW Demand based on Cycle | 5.845 | kWh/day | based on default for Cycle | L | 11.655 | 130 | 86.6667 | 78 | 0 | 0
COP based on EN 16147 | 2.4 |  |  | XL | 19.07 | 210 | 140 | 126 | 0 | 0
Capacity of Heat Pump | 1.35 | kW |  | XXL | 24.53 | 300 | 200 | 180 | 0 | 0
|  |  |  | 3XL | 46.76 | 520 | 346.6667 | 312 | 0 | 0
Efficiency for DEAP | 2.7695 |  | based on equation from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps, converting 15316-4-2:2008 SPF to SAP SPF | 4XL | 93.52 | 1040 | 693.3333 | 624 | 0 | 0
0
Reference Temperature | 55 | oC | [6 empty] | 0 | 0
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC | [6 empty] | WARNING: The Test Storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | WARNING: The test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency.
Fraction of Demand met by backup energy to meet temperature shortfall | 0.18182 |  | based on eqt 18 from EN 15316
DHW Demand for Dwelling | 2366.1086 | kWh
Required Running Hours | 1752.673 | hrs
Effective Bin Time | 8760 | hrs | based on eqt 7 from EN 15316
Difference between Req and Effective | 0
Fraction of Demand met by backup to meet operation hours shortfall | 0
Heat Pump Electricity | 698.9978 | kWh
Back Up Heater due to temperature shortfall | 430.2016 | kWh | Efficiency of Back up Water Heater adjusted relative to Direct Electric Heating
Back Up Heater due to operation shortfall | 0 | kWh | Efficiency of Back up Water Heater adjusted relative to Direct Electric Heating
Total Electricity Required for Water Heating | 1129.1994 | kWh
SPF | 2.0954
Renewable Contribution calculated in DEAP | 1236.9092 | kWh
Hot Water Provided by Heat Pump | 1935.907 | kWh
% Renewable | 100%
Renewable Contribution provided by Heat Pump | 1236.9092 | kWh
EN 255-3
DHW Demand for Dwelling | 2366.1086 | kWh
COP based on EN 255 | 0
Capacity of Heat Pump | 0 | kW
Reference Temperature | 0 | oC
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC
Fraction of Backup energy due to temperature shortfall | 1.1818 |  | based on eqt 18 from EN 15316
Electricity required by Heat Pump | #DIV/0! | kWh
Electricity required by Back Up Heater | 2796.3102 | kWh
Total Electricity Required for Water Heating | #DIV/0! | kWh
SPF | #DIV/0!
Renewable Contribution calculated in DEAP | #DIV/0! | kWh
Hot Water Provided by Heat Pump | -430.2016 | kWh
SPF - Heat Pump Only | #DIV/0!
Renewable Contribution provided by Heat Pump | #DIV/0! | kWh
EN 14511
DHW Demand for Dwelling | 2366.1086 | kWh
COP based on EN 14511 | 3
Efficiency Adjustment Factor | 1
SPF | 1.5
Total Electricity Required for Water Heating | 1577.4057 | kWh
Renewable Contribution calculated in DEAP | 0 | kWh
Hot Water Provided by Heat Pump | 1183.0543 | kWh
Electricity required by Heat Pump | 394.3514 | kWh
Renewable Contribution provided by Heat Pump | 197.1757 | kWh

## Meteorological data
| 16 | Design Temperature |  |  |  | DHW Energy kWh
Taken as 16 based on EN14825
Outdoor temperature bin (deg C) | Name IRL_Dublin_IWEC2.epw Description IWEC2- ASHRAE Latitude 53.43000031 Longitude -6.25 Time Zone -0.419999987 Year 2000 Ground Source Temperature 11.97182465 Altitude 0 Number of hours per bin | Cumulative Hrs | Heating Degree Hrs | Cumulative heating Degree Hrs | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8
-12 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0
-5 | 0 | 0 | 0 | 0 | 0 | 0
-4 | 0 | 0 | 0 | 0 | 0 | 0
-3 | 4 | 4 | 76 | 76 | 0.0013629 | 0.00045662
-2 | 14 | 18 | 252 | 328 | 0.0045191 | 0.0015982
-1 | 44 | 62 | 748 | 1076 | 0.013414 | 0.0050228
0 | 112 | 174 | 1792 | 2868 | 0.032136 | 0.012785
1 | 146 | 320 | 2190 | 5058 | 0.039273 | 0.016667
2 | 222 | 542 | 3108 | 8166 | 0.055736 | 0.025342
3 | 323 | 865 | 4199 | 12365 | 0.075301 | 0.036872
4 | 400 | 1265 | 4800 | 17165 | 0.086079 | 0.045662
5 | 446 | 1711 | 4906 | 22071 | 0.087979 | 0.050913
6 | 545 | 2256 | 5450 | 27521 | 0.097735 | 0.062215
7 | 603 | 2859 | 5427 | 32948 | 0.097323 | 0.068836
8 | 658 | 3517 | 5264 | 38212 | 0.0944 | 0.075114
9 | 681 | 4198 | 4767 | 42979 | 0.085487 | 0.07774
10 | 639 | 4837 | 3834 | 46813 | 0.068755 | 0.072945
11 | 660 | 5497 | 3300 | 50113 | 0.059179 | 0.075342
12 | 610 | 6107 | 2440 | 52553 | 0.043757 | 0.069635
13 | 582 | 6689 | 1746 | 54299 | 0.031311 | 0.066438
14 | 481 | 7170 | 962 | 55261 | 0.017252 | 0.054909
15 | 502 | 7672 | 502 | 55763 | 0.0090024 | 0.057306
16 | 383 | 8055 | 0 |  |  | 0.043721
17 | 259 | 8314 |  |  |  | 0.029566
18 | 170 | 8484 |  |  |  | 0.019406
19 | 112 | 8596 |  |  |  | 0.012785
20 | 67 | 8663 |  |  |  | 0.0076484
21 | 37 | 8700 |  |  |  | 0.0042237
22 | 27 | 8727 |  |  |  | 0.0030822
23 | 20 | 8747 |  |  |  | 0.0022831
24 | 13 | 8760 |  |  |  | 0.001484
25 | 0 | 8760 |  |  |  | 0
26 | 0 | 8760 |  |  |  | 0
27 | 0 | 8760 |  |  |  | 0
28 | 0 | 8760 |  |  |  | 0
29 | 0 | 8760 |  |  |  | 0
30 | 0 | 8760 |  |  |  | 0
31 | 0 | 8760 |  |  |  | 0
32 | 0 | 8760 |  |  |  | 0
33 | 0 | 8760 |  |  |  | 0
34 | 0 | 8760 |  |  |  | 0
35 | 0 | 8760 |  |  |  | 0
0

## Rpt
DEAP Report
DEAP Workbook: |  | 44927
Inputs and results, with selected intermediate results shown in italics
Details not applicable for this dwelling are grayed out.
Print out 'Proj' worksheet separately if required.
Dwelling dimensions |  |  |  |  | TGD L version |  | 2019
|  | Area [m2] | Height [m]
Ground floor |  | 81 | 2.45
First floor |  | 0 | 0
Second floor |  | 0 | 0
Third and other floors |  | 0 | 0
Total floor area [m2] |  | 81
Dwelling volume [m3] |  | 198.45
Living area [m2] |  | 40.5
Ventilation
Number of chimneys |  |  |  |  | 0
Number of open flues |  |  |  |  | 0
Number of intermittent fans and passive vents |  |  |  |  | 1
Number of flueless gas fires |  |  |  |  | 0
Is there a draught lobby on main entrance? |  |  |  |  | No
Number of storeys in the dwelling |  |  |  |  | 2
Has an air permeability test been carried out? |  |  |  |  | Yes | 1
If no | Not applicable
| Structure type |  |  |  |  | Masonry
| Is there a suspended wooden ground floor? |  |  |  |  | None
| Percentage of windows and doors draughtstripped [%] |  |  |  |  | 100
If yes | :
| Air permeability [m3/h.m2 at 50 Pa] |  |  |  |  | 3
End if
Number of sides sheltered |  |  |  |  | 2
Ventilation method |  |  |  |  | Whole-house extract ventilation | [6 empty] | 4
Effective air change rate [ac/h] |  |  |  |  | 0.5
Ventilation heat loss [W/K] |  |  |  |  | 32.7443
Permeability test carried out and meets guidelines in TGD L? | [5 empty] | Complies
For mechanical ventilation, other than positive input ventilation from loft: | [6 empty] | :
| Is measured "PCDB" data available? | [6 empty] | Yes
| Manufacturer and model | [6 empty] | 0
| Specific fan power [W/(l/s)] | [6 empty] | 0.2
| Heat exchanger efficiency [%] | [6 empty] | -
Windows
Orientation |  |  |  | East/West | South | North | SE/SW | South | North | North | North | Horizontal
Orientation ID |  |  |  | 3 | 5 | 1 | 4 | 5 | 1 | 1 | 1 | 6
Area [m2] |  |  |  | 10.8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
U-value [W/m2 K] |  |  |  | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0
Is U-value a manufacturer's certified value? |  |  |  | Yes | Yes | Yes | - | - | - | - | - | -
If yes:
| Manufacturer and model |  |  | - | - | - | - | - | - | - | - | -
| Solar energy transmittance |  |  | 0.6 | 0.6 | 0.6 | - | - | - | - | - | -
End if
Correction for roof window and/or metal frame if applicable (Table 6a, notes 1 and 2).
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overshading ID |  |  |  | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Frame factor (Table 6c) [-] |  |  |  | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Window type ID |  |  |  | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Fabric
Exposed element type |  |  | Area | U-value | AU | Comment (optional) |  |  | Element type
|  |  | [m2] | [W/m2 K] | [W/K] |  |  |  | (for assessing TGD L conformity)
Windows/rooflights |  |  | 19.8 | 0.86873 | 17.2008 | -
Doors |  |  | 1.85 | 1.5 | 2.775 | -
Floor |  |  | 0 | 0 | 0 | - |  |  | No underfloor heating
Floor (type 2) |  |  | 0 | 0 | 0 | - |  |  | No underfloor heating
Floor (type 3) |  |  | 0 | 0 | 0 | - |  |  | No underfloor heating
Walls |  |  | 24.3 | 0.13 | 3.159 | - |  |  | Wall relevant for TGD L fabric compliance check
Walls (type 2) |  |  | 11.5 | 0.194 | 2.231 | - |  |  | Wall relevant for TGD L fabric compliance check
Walls (type 3) |  |  | 0 | 0 | 0 | - |  |  | Wall relevant for TGD L fabric compliance check
Walls (type 4) |  |  | 0 | 0 | 0 | - |  |  | Wall relevant for TGD L fabric compliance check
Walls (type 5) |  |  | 0 | 0 | 0 | - |  |  | Wall relevant for TGD L fabric compliance check
Roof |  |  | 0 | 0 | 0 | - |  |  | Pitched roof - Insulation at ceiling
Roof (type 2) |  |  | 0 | 0 | 0 | - |  |  | Pitched roof - Insulation at ceiling
Roof (type 3) |  |  | 0 | 0 | 0 | - |  |  | Pitched roof - Insulation at ceiling
Roof (type 4) |  |  | 0 | 0 | 0 | - |  |  | Pitched roof - Insulation at ceiling
Roof (type 5) |  |  | 0 | 0 | 0 | - |  |  | Pitched roof - Insulation at ceiling
Total area of elements [m2] |  |  | 57.45
Heat loss via plane elements [W/K] |  |  |  |  | 25.3658
Factor for thermal bridging [W/m2 K] |  |  |  |  | 0.05
Fabric heat loss [W/K] |  |  |  |  | 28.2383
Dwelling heat loss coefficient [W/K] |  |  |  |  | 60.9825
Heat loss parameter, HLP [W/K m2] |  |  |  |  | 0.75287
Water heating
Are there distribution losses? |  |  |  | Yes
Distribution loss [kWh/y] |  |  |  | 263.3354
Are there storage losses? |  |  |  | Yes | 1
If yes | :
| Water storage volume [litres] | [5 empty] | 180
| Is manufacturer's declared loss factor available? | [5 empty] | No | 0
| If yes | Not applicable
|  | Manufacturer and model name |  |  |  |  | -
|  | Manufacturer's declared loss factor [kWh/day] |  |  |  |  | 1.2
| If no | :
|  | Insulation type on hot water store |  |  |  |  | Factory insulated
|  | Insulation thickness [mm] |  |  |  |  | 100
End if
| Temperature factor unadjusted (Table 2) |  |  |  |  | 0.6
| Temperature factor multiplier (from Table 2 notes) |  |  |  |  | 0.9
End if
Is there a solar water heating system? | [5 empty] | No | 0
If yes | Not applicable
| Solar DHW input, Qs [kWh/y] |  |  |  |  | 0 |  | Solar fraction [%] |  | 0
| Is solar water heating pump PV powered? |  |  |  |  | No
End if
Primary circuit loss [kWh/y] (Table 3) | [7 empty] | 360
Additional loss for combi boiler [kWh/y] (Table 3a) | [7 empty] | 0
Electricity consumption of electric keep-hot facility of combi boiler [kWh/y] (Table 4f) | [7 empty] | 0
Is supplementary electric immersion heating is used in summer? | [7 empty] | No
Output from main water heater [kWh/y] | [5 empty] | 2366.1086
Output from supplementary heater [kWh/y] | [5 empty] | 0
Heat gains from water heating system [W] | [5 empty] | 122.3925
Is hot water storage indoors or in group heating scheme? | [5 empty] | Yes
Lighting
Annual energy used for lighting, EL [kWh/y] | [5 empty] | 185.9537
Internal gains
Net internal gains [W] | [5 empty] | 415.8782
Heat use
Living area fraction [-] |  |  |  | 0.5
Thermal mass category of dwelling |  |  |  | Medium
Heat use [kWh/y] |  |  |  | 578.757
Space heating
Control and responsiveness
Temperature adjustment (Table 4e), where appropriate [C] | [5 empty] | 0
Heating system control category (Table 4e) | [5 empty] | 3
Heating system responsiveness category (Table 4a or 4d) | [5 empty] | 1
Pumps/fans | [6 empty] | Enter | If present, |  | If present,
[7 empty] | number | is boiler controlled |  | inside
[7 empty] | present | by room thermostat? |  | dwelling?
Central heating pump (supplying hot water to radiators or underfloor system) | [6 empty] | 1 |  | Yes
Oil boiler - pump (supplying oil to boiler and flue fan) | [6 empty] | 0 |  | - | -
Gas boiler - flue fan (if fan assisted flue) | [6 empty] | 0
Is there a warm air heating system present? | [5 empty] | No
Emission efficiency
Is main heat emission system within an envelope element? (e.g. underfloor heating in ground floor) | [8 empty] | - | 0
| If yes, U-value of envelope element [W/m2 K] | [7 empty] | 0
Type of main heating system |  |  |  | Individual system |  |  |  | 1
Energy requirements - individual heating systems | [5 empty] | :
Space Heating
Efficiency of main heating system [%] (including Efficiency Adjustment Factor) | [8 empty] | 398.8614
Fraction of heat from secondary / supplementary system (from Table 7, Table 10 or Appendix F) | [8 empty] | 0
Efficiency of secondary / supplementary heater(s) [%] (from Table 4a or Appendix E) | [8 empty] | 0
Water heating
Efficiency of main water heater [%] (from HARP or from Table 4a or 4b) | [8 empty] | 209.5386
Cooling
SEER | [8 empty] | -
Fuel data |  |  | Fuel
Space heating - main |  |  | electricity
Space heating - secondary |  |  | -
Water heating - main |  |  | electricity
Water heating - supplementary |  |  | -
Photovoltaic/ Wind Turbine |  |  | 0 | kWh/y
Solar Thermal |  |  | 0 | kWh/y
[7 empty] | Primary | CO2 |  | Delivered
Renewable and energy-saving technologies | [6 empty] | energy | factor |  | energy
Type 1 | Description | [5 empty] | factor [-] | [kg/kWh] |  | [kWh/y]
| Energy produced or saved | [5 empty] | 1.75 | 0.224 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Type 2 | Description |  | -
| Energy produced or saved | [5 empty] | 0 | 0 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Type 3 | Description |  | -
| Energy produced or saved | [5 empty] | 0 | 0 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Energy requirements - group/community heating scheme | [5 empty] | Not applicable
Secondary space heating
Fraction of heat use from secondary / supplementary system (use value from Table 7, Table 10 or Appendix F) | [10 empty] | 0
Generation efficiency of secondary / supplementary heating system [%] (use value from Table 4a or Appendix E) | [10 empty] | 0
Main (group heating) system
Is charging based on heat consumed? | [6 empty] | Yes
Distribution loss factor [-] (Table 9) | [6 empty] | 0
Fraction of heat from CHP unit or fraction of heat recoverd from power station | [6 empty] | 0
Boilers
(If the fraction of heat from boilers is zero, this section is irrelevant).
| Heat source type |  | Fuel |  |  |  | Efficiency | Percent of
[7 empty] | [%] | heat [%]
| Central Boiler |  | mains gas |  |  |  | 0 | 0
| Central Boiler |  | wood pellets - bulk supply, for main htg |  |  |  | 0 | 0
| Heat Pump |  | electricity |  |  |  | 0 | 0
| Heat Pump |  | electricity |  |  |  | 0 | 0
| Solar heating system | [6 empty] | 0
CHP or waste heat from power stations
(If the fraction of heat from CHP/waste heat is zero, this section is irrelevant).
| System type |  |  |  |  | District Heating |  |  |  | 2
If CHP
|  | Electrical efficiency of CHP unit (e.g. 0.3) from operational records or the CHP design specification [-] | [8 empty] | 0
|  | Heat efficiency of CHP unit (e.g. 0.5) from operational records or the CHP design specification [-] | [8 empty] | 0
|  | Fuel type |  |  |  | mains gas
If Waste Heat
|  | Renewable Primary Energy Factor |  |  |  | 0
|  | Non Renewable Primary Energy Factor |  |  |  | 0
|  | CO2 Emission Factor |  |  |  | 0
Fuel data |  |  | Fuel
Space heating - secondary |  |  | -
Photovoltaics/ Wind Turbine |  |  | 0 | kWh/yr
Solar |  |  | 0 | kWh/yr
[7 empty] | Primary | CO2 |  | Delivered
Renewable and energy-saving technologies | [6 empty] | energy | factor |  | energy
Type 1 | Description |  | - |  |  |  | factor [-] | [kg/kWh] |  | [kWh/y]
| Energy produced or saved | [5 empty] | 0 | 0 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Type 2 | Description |  | -
| Energy produced or saved | [5 empty] | 0 | 0 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Type 3 | Description |  | -
| Energy produced or saved | [5 empty] | 0 | 0 |  | 0
| Energy consumed | [5 empty] | 0 | 0 |  | 0
Results
|  |  |  | Delivered energy | Primary energy | CO2 emissions
|  |  |  | [kWh/y] | [kWh/y] | [kg/y]
Space heating - main |  |  |  | 133.9636 | 234.4363 | 30.0079
Space heating - secondary |  |  |  | 0 | 0 | 0
Water heating - main |  |  |  | 1129.1994 | 1976.0989 | 252.9407
Water heating - supplementary |  |  |  | 0 | 0 | 0
Cooling |  |  |  | 0 | 0 | 0
Pumps, fans |  |  |  | 100.4218 | 175.7382 | 22.4945
Energy for lighting |  |  |  | 185.9537 | 325.419 | 41.6536
Renewable and energy-saving technologies
CHP input (individual heating systems only) |  |  |  | 0 | 0 | 0
CHP electrical output (individual heating system only) |  |  |  | 0 | 0 | 0
Photovoltaic/ Wind Turbine |  |  |  | 0 | 0 | 0
Type 1 |  |  |  | 0 | 0 | 0
Type 2 | - |  |  | 0 | 0 | 0
Type 3 | - |  |  | 0 | 0 | 0
Total |  |  |  | 1549.5385 | 2711.6924 | 347.0966
per m2 floor area |  |  |  | 19.1301 | 33.4777 | 4.2851
Building Energy Rating [kWh/m2 y] |  |  |  |  | 33.4777 | A2
Check conformity with MPEPC and MPCPC requirements in TGD L | [6 empty] | 2019
Max permitted
EPC |  | 0.25483 | 0.3 | Complies
CPC |  | 0.17144 | 0.35 | Complies
RER |  | 0.37647 | 0.2 | Complies

## Sheet1
This blank worksheet may be used for supporting calculations if desired