## Notes
Yes
No
Heat loss calculation and radiator sizing for heat pump systems
Version 1.1
Calculation of the heat loss for each room forms the basis for the design and sizing of a heating system. While a rule of thumb approach may have been widely used in the past for the sizing of domestic boiler systems, in the case of more complex systems such as those with heat pumps, this approach is not suitable.
The aim of these notes is to assist the contractors carrying out the design of heat pump systems for domestic retrofit. This is a summary of some of the procedures involved in the design of heating systems based on heat pump. It is not a comprehensive guide on heating system design. For more comprehensive guidance, and for more details, please consult the following guide:
CIBSE HVDH Domestic Heating Design Guide, available from:
https://www.cibse.org/knowledge/knowledge-items/detail?id=a0q20000008I7odAAC
This guidance does not constitute an official SEAI procedure, and is given to assist contractors in carrying out a basic heat loss calculation for the purpose of supporting design or verification of the heat emitters' size. As the performance and efficiency of the heat pump system depends on the heat loss calculation, it is the contractor's responsibility to ensure that this is carried out correctly.
1. Heat Requirement
The heat required for a room depends mainly on two factors: the temperature you want to maintain the room at, and the rate of heat loss from that room. Additional heat sources should also be taken into account.
For the purpose of sizing heat emitters, heat losses must be calculated on a room by room basis. To calculate the heat loss from the room, the area of all floors, walls, windows and doors and their thermal characteristics (U-values, etc.) need to be taken into account. In addition, the ventilation heat losses need to be considered.
2. Example of room heat loss calculation
An example of how to carry out a heat loss calculation is provided in this spreadsheet. Contractors should note that SEAI is providing this as an example of how to carry out the calculation, and that they may choose to use other tools, as long as the calculation is in accordance to best practice, suitable for the purpose and not oversimplified.
Please also note that this is a basic calculator and you may need to adapt it suitably in some cases. When lines are duplicated or other changes are made, users must make sure that the formulae are correct.
The heat loss resulting from this calculation should be used as a basis for sizing radiators for individual rooms within a dwelling.
The following convention is used in the spreadsheet to indicate the type of cell:
Input cell | 21
Fixed value | -3
Calculated cell* | 0
* In some cases it may be useful to use the calculated cells as inputs, for example if the shape of the room is not rectangular and the area needs to be calculated outside the tool.
The tab "Room1" contains a calculation sheet filled in with example values, and the tab "Room2" contains a blank calculation sheet. The following paragraph explains some of the inputs required.
2.1. Design Temperatures
An “External design temperature” of -3 °C should be used when calculating heat losses on a room by room basis in the Irish climate.
The “Design room temperature” of the room must be entered. Suitable temperatures are provided in the table below.
|  | Room | Room Internal Design Temperature °C
|  | Lounge sitting room | 21
|  | Living room | 21
|  | Dining room | 21
|  | Kitchen | 18
|  | Breakfast room | 21
|  | Kitchen/breakfast | 21
|  | Hall | 18
|  | Cloakroom | 18
|  | Toilet | 18
|  | Utility room | 18
|  | Study | 21
|  | Games room | 21
|  | Bedroom | 18
|  | Bedroom/en suite | 18
|  | Bedsitting room | 21
|  | Bedroom/study | 21
|  | Landing | 18
|  | Bathroom | 22
|  | Shower room | 22
|  | Dressing room | 21
|  | Storeroom | 16
2.2. Ventilation Heat Loss
The ventilation rates (“number of air changes per hour ac/h”) for the individual room should be selected from the table below.
Air changes per hour
|  | Room | Older dwellings (pre 2005) | Newer dwellings (2005-2010) | Dwellings built to 2011 Part L or with air tightness tested to 7 m3/h·m2 or lower
|  | Sitting/Living/Dining/ Study/Breakfast room | 1.5 | 1 | 0.5
|  | Kitchen | 2.0* | 1.5* | 1.5*
|  | Hall | 2 | 1 | 0.5
|  | Cloakroom/WC | 2.0* | 1.5* | 1.5*
|  | Bathroom/Toilet/Shower room | 3.0* | 1.5* | 1.5*
|  | Utility room | 3.0* | 2* | 0.5*
|  | Study/Games room | 1.5 | 1.5 | 0.5
|  | Bedroom | 1 | 1 | 0.5
|  | Bedroom with en suite | 2 | 1.5 | 1
|  | Landing | 2 | 1 | 0.5
|  | Storeroom | 1 | 0.5 | 0.5
* Due allowance to be made where mechanical extract ventilation is present
The ventilation heat loss needs also to take account of chimney and open flues. Additional ventilation rates are provided in the table below:
|  | Room volume [m3] | Throat restrictor fitted to flue | Additional air changes per hour
|  | Up to 40 | NO | 5
|  |  | YES | 3
|  | 40-70 | NO | 4
|  |  | YES | 2
2.3. Fabric Heat Loss
Measurements | Dimensions of building elements should be based on on-site measurements or on architect’s plans when the building is undergoing modifications at the time of the heat pump system design. When following plans, the contractor must verify that the as-built dimensions are compatible with the calculations based on the plans.
External Walls and Roofs (Gross and Net areas) | The dimensions of Walls and Roofs are entered. The area of windows, doors and roof lights are then subtracted from the gross area of wall or roof in order to calculate the heat loss from that element (net area).
Internal Walls | Heat loss occurring within the home, from rooms heated at different temperatures (e.g. 21 ⁰C vs 18 ⁰C) has been neglected in this example.
Party Walls | Under normal conditions unheated adjoining properties will be at a temperature above the outside design temperature. In the absence of specific information 10°C shall be used for an unheated adjoining property, garage, or similar unheated spaces. The heat loss to adjoining spaces or properties that are heated at the same level as the room can be considered as zero.
U Values | Contractors are responsible for sourcing valid thermal performance data for the heat loss calculations. Possible sources for these values are:
· The SEAI Registered Technical Advisor, through the homeowner
· The DEAP methodology (DEAP manual)
· U value Tables in the CIBSE Domestic Heating Design Guide
Adjustments for Exposed Location and High Ceilings | The heat loss should be adjusted when the dwelling location is particularly exposed (e.g. located on a hill or extremely open location). An adjustment is also required when there are high ceilings (over 3m), only if the room will not be heated with underfloor heating.
3. Radiator Sizing
Most radiator outputs provided by the radiator manufacturers are based on boiler systems, and on a water-to-air temperature difference (ΔT) of 50⁰C
The higher the ∆T value, the higher the radiator output will be. Traditional gas or oil boilers operate with much higher flow and return temperatures than heat pumps, meaning there is a greater temperature difference between the water temperature and the air temperature. Flow temperatures for boilers are typically in the region of 60⁰C - 80⁰C, and return 50⁰C - 70⁰C. With a required room temperature of 20⁰C, the ΔT value is 40°C-55°C and so the radiator output is high.
Non-condensing boiler
Condensing boiler
In order to operate efficiently, the flow temperature of heat pumps must be much lower, at around 45°C. With a return temperature of 40°C, the ΔT value for a heat pump is therefore much lower, around 22.5°C:
Heat pump system
The lower temperature difference will reduce the output of the same radiator.
The following table is an example of information provided by the manufacturer:
|  | Radiator Height | Radiator Length |  | Heat Output at ΔT 50° [W]
|  |  | mm | inches
|  | 300mm | 400 | 16 | 186
|  |  | 800 | 31 | 382
|  |  | 1000 | 39 | 480
|  |  | 1200 | 47 | 578
|  |  | 1600 | 63 | 774
|  |  | 2000 | 79 | 969
Where radiators are to be installed for different ΔT values, the stated radiator outputs must be multiplied by a conversion factor to account for the different ΔT value. Manufacturers should be asked to provide heat outputs or conversion factors for different ΔT values.
In cases where it is not possible to source the conversion factor from the manufacturer, the values in the following table can be applied to outputs quoted at ΔT 50° to obtain the reduced outputs at the different ΔT. Please use conversion factors provided by the radiator’s manufacturer wherever available.
|  | ΔT | Multiply Output by
|  | Δ15° | 0.21
|  | Δ17.5° | 0.26
|  | Δ20° | 0.3
|  | Δ22.5° | 0.35
|  | Δ25° | 0.41
|  | Δ27.5° | 0.46
|  | Δ30° | 0.51
|  | Δ32.5° | 0.57
|  | Δ35° | 0.63
|  | Δ37.5° | 0.69
|  | Δ40° | 0.75
For example, where replacement radiators with a ΔT value of 25°C are being installed, and the stated output at Δ50°C is 480W, multiply by 0.41 to get the output for the replacement radiators.
e.g. 480 W x 0.41 = 197 W
The radiator output is now 197 W. This may mean you need to increase the size of the radiator to meet the heat requirement of the room depending on the heat loss calculated.
4. Important note on existing radiators
Replacing existing radiators with new ones may not be necessary in all cases of heat pump retrofit. However, it is likely that the existing radiators have been sized on the basis of a higher ΔT value (40°C-55°C). The output of the existing radiators at a lower ΔT value (20°C-25°C) will be much lower. The heat loss calculation and sizing verification is still needed where existing radiators are maintained to confirm that the existing radiators are sufficient to deliver the space heating required.
In cases when no manufacturer’s information is available, the heat output of existing radiators can be estimated based on the information in the guide “Heat Emitter Supplement to the Domestic Heating Design Guide”. Please note that the estimates in this guide are given for ΔT 50°, and will need to be converted as explained available from:
http://regulations.completepicture.co.uk/pdf/Mcs/Supplementary%20tables%20of%20heat%20emitter%20outputs.pdf
5. Other system design considerations
This guidance only covers some aspects of the heat emitter sizing. Contractors are responsible for all aspects of the heating system design, including those not covered by this document, such as pipework sizing, pressure loss calculation and circulator sizing to ensure a correct flow rate, sizing of the heat source.
6. Documents to be provided by contractors for Better Energy Homes grants for Heat Pump Systems
Contractors must refer to the SEAI Contractor’s Code of Practice for all product and installation requirements for the domestic grants. This also contains details of the documents required.
The Heat Pump Designer/Installer Sign-Off Sheet is available on the Contractor Support page of the SEAI website.
The Heating Design Details contain the list of heat emitters and are required to demonstrate that the whole heat pump system has been designed to meet the heat demand. Please see below an example of how this sheet should be filled out:
The heat emitters must be sized on the basis of the Design Flow temperature, so that the Total Output is equal or greater than the Total Heat Loss.

## Room1
ROOM | Kitchen/Dining room
Design Room Temp |  | 21 | Notes:
External Design Temp |  | -3
Design Temp Difference |  | 24
Ventilation Heat Loss |  |  | No. of air changes per hour ac/h | Room Volume (meters) |  |  | Amount of air to be heated per hour m3/h | Air change factor W/m3.K | Design Temp Diff ⁰C | Heat Loss Watts
|  |  |  | Length (m) | Width (m) | Height (m)
|  |  | 1.5 | 4.9 | 2.7 | 2.4 | 47.628 | 0.33 | 24 | 377.2138
Additional air changes due to Chimneys or Flues |  |  | 3 | For additional air changes see table in section 2.2. Ventilation Heat Loss |  |  | 95.256 | 0.33 | 24 | 754.4275
Fabric Heat Loss |  |  |  | Length (m) | Width (m) | Height (m) | Area m2 | U-Value W/m2.K | Design Temp Diff ⁰C
External Floor |  |  |  | 4.9 | 2.7 |  | 13.23 | 0.77 | 24 | 244.4904
External Wall (Gross area) |  |  |  | 7.6 |  | 2.4 | 18.24
Window |  |  |  |  | 1.1 | 1.05 | 1.155 | 1.6 | 24 | 44.352
Window |  |  |  |  | 1.1 | 1.05 | 1.155 | 1.6 | 24 | 44.352
External Door |  |  |  |  | 1.75 | 2.1 | 3.675 | 1.6 | 24 | 141.12
External Wall (Nett area) |  |  | (Subtract glazing and door areas from gross external wall area) |  |  |  | 12.255 | 0.27 | 24 | 79.4124
External Roof (Gross area) |  |  |  | 0 | 0 |  | 0
Rooflights |  |  |  |  | 0 | 0 | 0 | 0 | 24 | 0
External Roof (Nett area) |  |  | (Subtract roof glazing area from gross roof area) |  |  |  | 0 | 0 | 24 | 0
Party Wall Adjoining unheated space |  |  |  | 2.7 |  | 2.4 | 6.48 | 1.02 | 11 | 72.7056
Other |  |  |  | - | - | - | - | - | - | -
Design Heat Loss from Room (Sum of Watts for all elements) | [9 empty] | 1758.0737
Thermal Bridging | [9 empty] | 50.1146
Exposed Location? (If yes, 10% is added to the heat loss) | [8 empty] | Yes | 175.8074
High Ceiling - Is the room served by underfloor heating | [8 empty] | No | 0
Total room Heat Loss | [9 empty] | 1983.9956

## Room2
ROOM
Design Room Temp |  | Notes:
External Design Temp | -3
Design Temp Difference | 3
Ventilation Heat Loss |  | No. of air changes per hour ac/h | Room Volume (meters) |  |  | Amount of air to be heated per hour m3/h | Air change factor W/m3.K | Design Temp Diff ⁰C | Heat Loss Watts
|  |  | Length (m) | Width (m) | Height (m)
[6 empty] | 0 | 0.33 | 3 | 0
Additional air changes due to Chimneys or Flues |  |  | For additional air changes see table in section 2.2. Ventilation Heat Loss |  |  | 0 | 0.33 | 3 | 0
Fabric Heat Loss |  |  | Length (m) | Width (m) | Height (m) | Area m2 | U-Value W/m2.K | Design Temp Diff ⁰C
External Floor | [5 empty] | 0 |  | 3 | 0
External Wall (Gross area) | [5 empty] | 0
Window | [5 empty] | 0 |  | 3 | 0
Window | [5 empty] | 0 |  | 3 | 0
External Door | [5 empty] | 0 |  | 3 | 0
External Wall (Nett area) |  | (Subtract glazing and door areas from gross external wall area) |  |  |  | 0 |  | 3 | 0
External Roof (Gross area) |  |  | 0 | 0 |  | 0
Rooflights |  |  |  | 0 | 0 | 0 | 0 | 3 | 0
External Roof (Nett area) |  | (Subtract roof glazing area from gross roof area) |  |  |  | 0 | 0 | 3 | 0
Party Wall Adjoining unheated space | [5 empty] | 0 |  | -10 | 0
Other |  |  | - | - | - | - | - | - | -
Design Heat Loss from Room (Sum of Watts for all elements) | [8 empty] | 0
Thermal Bridging | [8 empty] | 0
Exposed Location? (If yes, 10% is added to the heat loss) | [7 empty] | Yes | 0
High Ceiling - Is the room served by underfloor heating | [7 empty] | No | 0
Total room Heat Loss | [8 empty] | 0

## Versions
Version | Changes compared to previous version
1.0 | First publication
1.1 | Changes from first publication: ▪ Changes to table of air changes per hour in section 2.2 ▪ Addition of table for air changes due to chimneys and flues ▪ Addition to room calculator to enter air changes due to chimneys and flues from table ▪ Correction of calculation in cell M39 (room calculator) ▪ Correction of calculation in cell M37 (room calculator) ▪ Correction of calculation in cell J30 (room calculator) ▪ Improved calculation for ceiling height ▪ Addition of heat loss due to thermal bridging (based on default) ▪ Correction of calculation in cell M40 (room calculator)