## Revision History
Revision | Description of Change | Date
1 | First Release | 2022-08-25
2 | Energy Balance Study published | 2022-09-13

## Instructions
Introduction
This Energy Balance Study [EBS] template can be used to meet the requirement to develop an energy balance as part of a project energy efficient design process. There is no requirement to utilise this template, however using it will assist in ensuring that the energy balance clause of the EXEED standard is met effectively. There are four tabs in this template namely, Data, EBS Report, Factors & Assumptions and Supplementary Information. The points below outline instructions on how to input data into each tab. The template has been prepopulated with example data to assist in outlining what detail is required in the energy balance study. This detail can be deleted and relevant sections populated with project specific information.
Number | Instruction
1 | On the Data tab, input details of energy sources, energy users, energy consumption and energy unit prices in the blue cells under the relevant headings of Table 1 and Table 2. Energy costs will update automatically in this worksheet. Table 1. Energy Source Data includes all energy consumption that is paid for by the organisation or any onsite generation through renewable energy sources. The energy unit price for onsite renewables shall be inputted at €0.00 per kWh. Ensure to include all energy sources related to the project. For CHP systems only include the energy which is consumed by the CHP system in Table 1. Additional data on CHP electrical and thermal performance can be included in the Factors & Assumptions or Supplementary Information tabs.
2 | Data from the Data tab is used to populate the EBS Report tab. The data in the EBS Report tab will populate automatically in this template. If additional rows are required for the inclusion of additional energy sources or users they can be added manually.
3 | Variables and conversion factors that are used for the calculations of energy and carbon flows or costs are included in the Factors & Assumptions tab. All factors and assumptions used in the development of the EBS should be included on this tab. These factors include but are not limited to energy unit process, CO2 conversion factors, equipment efficiencies e.g. boiler efficiency and chiller/heat pump coefficients of performance [COP]
4 | On the EBS Report tab, dropdowns are used for detailing how each element of the EBS has been calculated. Further details can be included in the comments and assumptions text boxes. It is important to give the evaluator sufficient detail to allow them to understand the calculation methodology and have confidence in the output of the EBS.
5 | The EBS Report tab also includes a section for the Determination of Significant Energy Users. It is important to detail here how the SEUs which have been chosen are aligned with the SEU criteria that have been set out in the Project Execution Plan. It can be seen in this example EBS that energy users have been combined in the SEU section i.e. Space Heating & Water Heating. Calculations can be included in relevant cells and explanations included in the Supplementary Information tab as required.
6 | An output of the EBS is a high level list of opportunities for improvement. The final section of the EBS Report includes a section for outlining opportunities that have been identified. Detailed calculation of opportunities is not required within the EBS however an outline of how these opportunities will be transferred to the Challenge & Analyse workshop should be recorded.
7 | The Supplementary Information tab has been included to allow for any additional information that may support the EBS and streamline its review by the evaluator.
Number | Notes
1 | When accounting for heat pumps delivering both space and water heating it is advised to include them as separate line items as the efficiency for delivering higher temperatures suitable for hot water production is lower than for space heating at (usually) lower temperatures. Any assumptions regarding heat pump COP should account for the actual flow temperatures required from the heat pump.
2 | Efficiency values for heating equipment using liquid/solid fuels should be stated in terms of gross efficiency. Gross efficiency can in most cases be easily approximated to Net efficiency using conversion factors found online.
3 | Please add a comment where appropriate to explain any assumptions regarding efficiency etc.
4 | The user is responsible for validity of inputs and checking calculations.

## Data
Table 1: Baseline Energy Source Input |  |  |  | January | February | March | April | May | June | July | August | September | October | November | December | Total | January | February | March | April | May | June | July | August | September | October | November | December | Total Cost
| Energy sources | Energy rates | Detail of Unit Price | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | € | € | € | € | € | € | € | € | € | € | € | € | €
1 | Grid electricity | 0.15 | Energy Unit Price and All Fixed & Variable Charges | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 1200000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 180000
2 | Natural gas - Boilers | 0.05 | Energy Unit Price and All Fixed & Variable Charges | 200000 | 200000 | 200000 | 200000 | 100000 | 100000 | 100000 | 100000 | 150000 | 200000 | 200000 | 200000 | 1950000 | 10000 | 10000 | 10000 | 10000 | 5000 | 5000 | 5000 | 5000 | 7500 | 10000 | 10000 | 10000 | 97500
3 | CHP Gas | 0.05 | Energy Unit Price and All Fixed & Variable Charges | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 1800000 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 90000
4 | Solar PV on-site electrical generation | 0 | N/A | 10000 | 15000 | 20000 | 25000 | 30000 | 35000 | 35000 | 30000 | 25000 | 20000 | 15000 | 10000 | 270000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Transport Fuel [DERV] | 0.18 | Energy Unit Price and All Fixed & Variable Charges | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 720000 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 10800 | 129600
7 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Totals |  |  |  | 520000 | 525000 | 530000 | 535000 | 440000 | 445000 | 445000 | 440000 | 485000 | 530000 | 525000 | 520000 | 5940000 | 43300 | 43300 | 43300 | 43300 | 38300 | 38300 | 38300 | 38300 | 40800 | 43300 | 43300 | 43300 | 497100
Table 2: Baseline Energy User Input
| Energy uses | kWhe | kWhth | Total kWh | Comment
1 | Space heating (gas boilers) | 20000 | 1000000 | 1020000
2 | Space heating (CHP unit) | 20000 | 800000 | 820000
3 | Space heating (heat pump) | 250000 | 0 | 250000
4 | Water heating (gas boilers) | 20000 | 450000 | 470000
5 | Water heating (CHP unit) | 20000 | 300000 | 320000
6 | Water heating (heat pump) | 200000 | 0 | 200000
7 | Lighting | 300000 | 0 | 300000
8 | Ventilation | 450000 | 0 | 450000
9 | Cooling (chiller) | 320000 | 0 | 320000
10 | Motors and drives | 200000 | 0 | 200000
11 | Pool | 150000 | 500000 | 650000
13 | Transport | 0 | 720000 | 720000
14 | Other | 157200 | 0 | 157200
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
Totals |  | 2107200 | 3770000 | 5877200
Note on B2: Guidance: On-site self generation from Solar PV and Wind etc. should also be accounted for as an energy source Take care to specify correct fuel e.g. natural gas or LPG; kerosene or fuel oil - see Factors & Assumptions tab for list of potential sources
Note on C2: Guidance: These rates should exclude VAT, unless VAT cannot be reclaimed. On-site electrical generation from sources such as Solar PV and Wind etc. should be given a rate of €0.00
Note on B16: Guidance: Use clear names so that a reader unfamiliar with the site can understand main uses. See Factors & Assumptions tab for list of potential uses.

## EBS Report
Energy Balance Study Approach
This energy balance study was developed by the EED Expert in collaboration with both the EED Owner and members of the design team. Given that this is an existing building that is undergoing a significant renovation, energy bill and meter data was used where available to determine energy consumption levels at both site and SEU levels. Several energy balances have been developed below including a: Balance of Energy Sources, Balance of Energy Costs, Balance of Energy Users, Balance of Electrical Energy Users & a Balance of Thermal Energy Users. This breakdown has been performed to get a detailed understanding of the energy consumption and uses across the site so as to assist in the identification of opportunities for improvement. Energy consumption values have been multiplied by average unit prices for each energy source to determine the balance of energy costs. Metered data and engineering calculations have then been used to get a further breakdown of energy uses across the site. This was essential to determine the significant energy users within the facility. These energy users have either been metered, or engineering calculations have been performed to determine an estimate of annual consumption. Engineering calculations have been developed through the surveying of plant or equipment whereby energy loads, load factors and estimate run hours have been applied to determine annualised consumption figures. In the case of thermal energy supply, equipment efficiencies such as boiler/CHP efficiencies or refrigeration/heat pump coefficient of performance [COP] values have been applied to energy source data. The energy balances are supplemented by monthly energy profiles for energy consumption and cost as illustrated in the bar charts below. Stacked bar charts are used to illustrate the monthly energy balance based on each energy source's contribution to monthly consumption. This method is used as fluctuations in the use of each energy source can be determined based on factors such as seasonality
Balance of Energy Sources | Energy Source Annual Profile |  |  |  |  | Comments & Assumptions
Natural gas is the most significant energy source at 63% of total energy consumption. The use of CHP in this system presents an opportunity for improvement given that it is expected that grid electricity will have less embodied carbon than natural gas as more renewables are brought online. In order to improve both energy and carbon performance it is recommended to remove CHP from the site. An additional opportunity is also evident in the electricity consumption annual profile. It is clear that there is very little seasonality in the electricity consumption values. Given that this is a building which contains a swimming pool and chiller system it would be expected that electricity consumption is seasonal with a peak over the warmer summer period. This is not evident, therefore further investigation is required into the operational controls of equipment.
Balance of Energy Costs | Energy Source Annual Cost Profile |  |  |  |  | Comments & Assumptions
While grid electricity is not the most significant energy source, it is the most significant energy cost as illustrated in the charts on the left. Given the scale the difference between electricity and gas costs it is recommended to review the electricity tariff structures for the business as there may be an opportunity to reduce the electricity unit price. No energy cost has been assigned to Solar PV in this instance as the PV system has already paid for itself since installation.
Balance of Energy Users | Energy User | Consumption [kWh] | % | Data Source |  | Comments & Assumptions
| Space heating (gas boilers) | 1020000 | 17.17% | Energy Bill |  | N/A
| Space heating (CHP unit) | 820000 | 13.8% | Metered Data |  | N/A
| Space heating (heat pump) | 250000 | 4.209% | Metered Data |  | N/A
| Water heating (gas boilers) | 470000 | 7.912% | Engineering Calculation |  | N/A
| Water heating (CHP unit) | 320000 | 5.387% | Engineering Calculation |  | Mass balance carried out based on other metered data and stated efficiencies
| Water heating (heat pump) | 200000 | 3.367% | Engineering Calculation |  | Calculated based on estimated volume per person per day and heat pump COP
| Lighting | 300000 | 5.051% | Engineering Calculation |  | Lighting calculation tool used: See lighting spreadsheet for granular detail.
| Ventilation | 450000 | 7.576% | Engineering Calculation |  | Fixed speed loads multiplied by operational hours.
| Cooling (chiller) | 320000 | 5.387% | Metered Data |  | N/A
| Motors and drives | 200000 | 3.367% | Engineering Calculation |  | Motors and drives survey carried out an calculation based on operating hours and recorded loads.
| Pool | 650000 | 10.94% | Metered Data |  | N/A
| Transport Fuel [DERV] | 720000 | 12.12% | Energy Bill |  | N/A
| Other | 220000 | 3.704% | Engineering Calculation |  | N/A
| Total | 5940000 | 100%
Balance of Electrical Energy Users | Energy User | Consumption [kWhe] | % | Data Source |  | Comments & Assumptions
| Space heating (gas boilers) | 20000 | 0.9491% | Metered Data |  | N/A
| Space heating (CHP unit) | 20000 | 0.9491% | Engineering Calculation |  | Calculated based on estimated volume per person per day and heat pump COP
| Space heating (heat pump) | 250000 | 11.86% | Engineering Calculation |  | Lighting calculation tool used: See lighting spreadsheet for granular detail.
| Water heating (gas boilers) | 20000 | 0.9491% | Engineering Calculation |  | Fixed speed loads multiplied by operational hours.
| Water heating (CHP unit) | 20000 | 0.9491% | Metered Data |  | N/A
| Water heating (heat pump) | 200000 | 9.491% | Engineering Calculation |  | Motors and drives survey carried out an calculation based on operating hours and recorded loads.
| Lighting | 300000 | 14.24% | Metered Data |  | N/A
| Ventilation | 450000 | 21.36% | Engineering Calculation |  | N/A
| Cooling (chiller) | 320000 | 15.19%
| Motors and drives | 200000 | 9.491%
| Pool | 150000 | 7.118%
| Other | 157200 | 7.46%
| Total | 2107200 | 100%
Balance of Thermal Energy Users | Energy User | Consumption [kWht] | % | Data Source |  | Comments & Assumptions
| Space heating (gas boilers) | 920000 | 23.55% | Engineering Calculation |  | Boiler efficiency from data sheet used.
| Space heating (CHP unit) | 441600 | 11.3% | Engineering Calculation |  | CHP thermal efficiency from data sheet used.
| Space heating (heat pump) | 1425000 | 36.48% | Metered Data |  | Heat pump COP from data sheet used.
| Water heating (gas boilers) | 432400 | 11.07% | Engineering Calculation |  | Boiler efficiency from data sheet used.
| Water heating (CHP unit) | 165600 | 4.239% | Metered Data |  | CHP thermal efficiency from data sheet used.
| Water heating (heat pump) | 62000 | 1.587% | Metered Data |  | Heat pump COP from data sheet used.
| Pool | 460000 | 11.77% | Metered Data |  | Heat meter on the heating loop to the pool.
| Total | 3906600 | 100%
Determination of Significant Energy Users
As detailed in the project execution plan, any energy user which consumes in excess of 5% of total energy consumption will be deemed significant. Where 80% of total site consumption has not been met with significant energy users, any user which is less than 5% and where it is determined that there is significant opportunity to improve energy performance will be included in the SEU list. The SEU's below account for 96% of total consumption. Motors & Drives have not been included as an SEU as they account for less than 5% of total consumption, and it was determined during the study that a project was carried out in the past 12 months to replace motors and drives with VSD controlled super premium efficiency units.
| SEU | Electricity [kWh] | Fuel Use [kWh] | Total Energy [kWh] | % of Total | Commentary on How SEU Criteria Apply
| Space Heating | 250000 | 1883002.2075 | 2133002.2075 | 35.91% | Combined space heating users account for greater than 5% of consumption
| Water Heating | 200000 | 801125.8278 | 1001125.8278 | 16.85% | Combined water heating users account for greater than 5% of consumption
| Pool | 300000 | 460000 | 760000 | 12.79% | This user accounts for >= 5% of consumption
| Cooling [chillers] | 320000 | 0 | 320000 | 5.387% | This user accounts for >= 5% of consumption
| Lighting | 300000 | 0 | 300000 | 5.051% | This user accounts for >= 5% of consumption
| Ventilation | 450000 | 0 | 450000 | 7.576% | This user accounts for >= 5% of consumption
| Transport Fuel [DERV] | 0 | 720000 | 720000 | 12.12% | This user accounts for >= 5% of consumption
| Total | 1820000 | 3864128.0353 | 5684128.0353 | 95.69% | -
Opportunities for Improvement
Several opportunities have been identified as part of this energy balance study. All opportunities will be incorporated into the Challenge & Analyse process as deemed appropriate. These opportunities include:
1. The potential to remove CHP from the site given that grid electricity will have lower embodied carbon in the coming years.
2. The potential for the replacement of the chiller with a heat pump in order to recover heat for use in the pool.
3. The potential to challenge the electrical base load given that seasonality is expected in monthly profile.
4. 12% of total energy could be decarbonised by switching from diesel vehicles to electric vehicles.

## Factors & Assumptions
Parameter | Value | Unit | Information Source/Justification for Use
Grid Electricity Unit Price | 0.15 | €/kWh | Annual average from energy bills
Natural Gas Unit Price | 0.05 | €/kWh | Annual average from energy bills
Gas Boiler Efficiency (Gross) | 92% | - | Product data sheet
Heat Pump COP - Space Heating | 5.7 | - | Product data sheet
Heat Pump COP - Hot Water | 3.1 | - | Product data sheet
CHP Electrical Efficiency (Gross) | 35.4% | - | Product data sheet
CHP Thermal Efficiency (Gross) | 55.2% | - | Product data sheet
CHP Efficiency (Gross) | 90.6% | - | Product data sheet
Chiller COP | 5.52 | - | Product data sheet
Potential Energy sources: |  | Potential Energy Users
Biodiesel |  | Space Heating
Biogas |  | Space Cooling
Biogasoline/Bioethanol |  | Ventilation – Natural
CHP - Electricity Generated |  | Ventilation – Mechanical
Coal |  | Lighting
Diesel/Gas Oil/Marked Gas Oil |  | Energy used for Heat production
Electricity - grid |  | Energy used for Cold production (refrigeration)
Geothermal/Ambient heat |  | Electromechanical use of energy
Heat Recovery Systems |  | Mechanical use of energy
Heavy Fuel Oil |  | Electric appliances
Hydroelectric |  | Water Heating
Kerosene |  | Others
Liquid Petroleum Gas (LPG)
Meat and bonemeal
Natural gas
Peat
Petroleum coke
Pure Plant Oil
Solar Photovoltaic (PV)
Solar Thermal
Wind Turbines
Wood Chip
Wood Logs
Wood Pellets
Wood Waste
Wood/Biomass

## Supplementary Information
Supplementary Information