## Cov
Dwelling Energy Assessment Procedure (DEAP) heat pump methodology update
Irish official method for rating the energy performance of dwellings
For use alongside DEAP 4
Date: August 2020
Rev 1.2 | Published version
Instructions for use: 1) Complete the DEAP assessment as far as the heat sources entries in DEAP software/workbook. This includes dimensions, fabric, windows, water heating (not including hot water heat source) storage/controls/distribution and space heating controls. 2) Complete the heat pump designer/installer form 3) Complete the yellow cells in the "DEAPEntries" tab 4) Complete the yellow cells in the HP tab 5) Transfer results to DEAP software as per guidance document 6) Calculate adjusted renewable energy ratio for NEW dwellings (see guidance document) NB Guidance document details cases where this heat pump should and should not be used.
Disclaimer & Copyright
Copyright to the Calculation Workbook is owned by The Sustainable Energy Authority of Ireland.
Apart from normal data entry, you may not make changes to the Calculation Workbook. You may not make alterations to its
structure, calculation procedures or contained data.
Neither SEAI, its consultants, suppliers nor any of their employees shall be held liable for any loss or
damage caused by the Calculation Workbook.
© 2006-2020 The Sustainable Energy Authority of Ireland. All rights reserved.

## Code
Overview of workbook
Cell shading
(based on Excel's standard colour palette)
Background colours used in data cells on the worksheets signify the following.
| Colour |  | Cell category
| Yellow |  | User inputs
| Blue |  | Main calculated results
| Green |  | Constants
| None |  | Intermediate calculated data
Use of this workbook
A calculation using this workbook should work sequentially through the individual spreadsheets as follows, leading ultimately to the display of results in the ‘Results’ worksheet:
| Worksheet | Main user entry actions |  | Visible calculated outcome
| Proj | Enter administrative details of the project |  | As entered
| DEAPEntries | Enter fields as shown in this tab, taken from the DEAP software and design data |  | Heat pump calculation results to be used in DEAP Adjusted renewable energy ratio.
| HP 1/2/3 | For each of heat pumps 1, 2, 3. Enter Manufacturer, model, test standard, test data of heat pumps, run hours and design flow temperature of heat pumps. |  | Efficiency of Space Heating Heat Pump, Water Heating Heat Pump, Renewable Contribution. Used in "DEAPEntries" tab above
| Heating Calc 1/2/3 | For each of heat pumps 1, 2, 3. None |  | Space Heating calculations for Heat Pump
| DHW Calc 1/2/3 | For each of heat pumps 1, 2, 3. None |  | Water Heating calculations for Heat Pump
| Meteorological Data | None |  | Bin data for heat pump calculation
| Space and water standards ID tabs 1/2/3 | For each of heat pumps 1, 2, 3. No user entries, but useful to see which standards apply to which heat pump types. |  | Used by this tool to identify erroneous heat pump types or erroneous standards selections

## Proj
Project
Project details
Dwelling type
Address
Eircode
MPRN Number
Date of assessment
Assessor details
Name
Title
Company
Phone
Email
Address
Comments

## DEAPEntries
Inputs from DEAP ¯ User to populate yellow cells below and in HP 1/2/3 tabs.
Description: | Value: |  |  | Unit: | Guidance Notes:
Total heat loss (W/K) taken from DEAP |  |  |  | W/K | Sourced from DEAP "results" tab (or DEAP workbook Fab tab). This is the sum of heat losses from fabric + ventilation + windows
Annual space heat requirement (total) |  |  |  | kWh | Sourced from DEAP: View assessment: Gains/losses (or SH tab in DEAP workbook) |  | Main space heating total | 0 | kWh
Floor Area of Dwelling |  |  |  | m2 | Sourced from DEAP: Building: Floors tab (or Dim tab in DEAP workbook)
Living area of dwelling |  |  |  | m2 | Sourced from DEAP: Building: Floors tab (or Dim tab in DEAP workbook)
Percentage of space heat from secondary system |  |  |  | % | Sourced from DEAP: Space heating: heat sources (or ER1/ER2 tab in DEAP workbook)
Fraction of heat from CHP |  |  |  | 0<=fraction <1 | Sourced from DEAP: Space heating: heat sources (or ER1/ER2 tab in DEAP workbook)
Output from main water heater |  |  |  | kWh | Sourced from DEAP: View assessment: Water (or WH tab in DEAP workbook) |  | Main space heating total | 0 | kWh
For Group Heating: Is charging based on heat consumed? | No |  |  |  | Sourced from DEAP: Space heating: heat sources (or ER2 tab in DEAP workbook) |  | Flat rate charge factor (set to 1 if not group heating) | 1
Electricity Primary Energy Factor | 2.08 |  |  |  | Sourced from DEAP: View assessment: Results (or Fuel tab in DEAP workbook) |  | Total main heating | 0 | kWh
Volume of DHW Storage |  |  |  | litres | Sourced from DEAP: Water Heating: options and storage (or WH tab in DEAP workbook)
Description: | Heat pump # 1 | Heat pump # 2 | Heat pump # 3 |  |  |  |  | 1 | 2 | 3 | Any
Type of space heating heat pump | Heat Pump | None | None |  |  |  | Space Heating served by HP | TRUE | FALSE | FALSE | TRUE
Type of water heating heat pump | Heat Pump | None | None |  |  |  | Hot Water served by HP | TRUE | FALSE | FALSE | TRUE
% main space heat provided by each heat pump based on system design | 0% | 0% | 0% | Total percentage=0% | Error: heat pump expected to provide 100% of main space heating |  | Total main space heating / total main heating | #DIV/0! |  |  | Source proportions of space heat from plant design details or operational records
% main water heat provided by each heat pump based on system design | 0% | 0% | 0% | Total percentage=0% | Error: heat pump expected to provide 100% of main water heating |  | Total main water heating / total main heating | #DIV/0! |  |  | Source proportions of water heat from plant design details or operational records
Is heat pump source preconditioned? | No | No | No |  | If heat pump source is preheated by another heat source other than exhaust air or ambient energy (e.g. a heat pump or boiler etc)
Is the Heat Pump part of a Group Heating Scheme | No | No | No | Individual heating applies | Sourced from DEAP: Space heating: Controls and responsiveness tab (or Sh tab in DEAP workbook) |  | Any group heating heat pumps present? | FALSE
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate |  |  |  | m3/h | Sourced from DEAP:Ventilation tab (or Vent tab in DEAP workbook) and divided between up to three Exhaust Air systems
RESULTS: Outputs for use in DEAP. ¯ User must manually transfer these to DEAP software.
Description: |  | Error: check entries |  | Unit: | Guidance Notes:
Efficiency of space heating heat pump + backup | #DIV/0! |  |  | [%] | Enter in DEAP: Space heating: heat source as heating system efficiency (or DEAP Workbook ER1/2). For group heating system, always enter under "heating system 1".
Space heating fuel type | Electricity |  |  |  | Enter in DEAP: Space heating: heat source as fuel (or DEAP Workbook ER1/2 tab). Gas fired heat pumps treated as natural gas / LPG boilers (with efficiency as derived by this calculation). For group heating system, always enter under "heating system 1".
Efficiency of water heating heat pump + backup | #DIV/0! |  |  | [%] | Enter in DEAP: Water heating: heat source as heating system efficiency (or DEAP Workbook ER1/2). For group heating system, always enter under "heating system 2".
Water heating fuel type | Electricity |  |  |  | Enter in DEAP: Water heating: heat source as fuel (or DEAP Workbook ER1/2 tab). Gas fired heat pumps treated as natural gas / LPG boilers (with efficiency as derived by this calculation). For group heating system, always enter under "heating system 2".
Efficiency adjustment factor for space heating and water heating | 1 |  |  |  | Always set to one when using this heat pump calculator
Group heating % of heat from space heating | n/a for individual system |  |  | [%] | Enter in DEAP: Space heating: heat source as proportion of heat alongside heat pump space heating efficiency (or DEAP Workbook ER1/2 tab space heating proportion of heat from heat pump). Total proportion of heat MUST be 100% in DEAP. For group heating system, always enter under "heating system 1".
Group heating % of heat from water heating | n/a for individual system |  |  | [%] | Enter in DEAP: Space heating: heat source as proportion of heat alongside heat pump water heating efficiency (or DEAP Workbook ER1/2 tab water heating proportion of heat from heat pump). Total proportion of heat MUST be 100% in DEAP. For group heating system, always enter under "heating system 2".
Additional errors and warnings: |  |  |  |  | If this error is shown, the heat pump test temperatures indicate that the proportion of water heating set by the user is too high
Additional errors and warnings: | #VALUE! |  |  |  | If this warning is shown, the system designer should review the proportions of heat from the heat pump and selection of heat pump if possible (e.g. maybe larger capacity is needed) to reduce the level of heating met by backup heater
Additional errors and warnings: |  |  |  |  | As per guidance document, only one heat pump may use test standard I.S. EN 14825/14511 for water heating.
Additional errors and warnings: |  |  |  |  | As per guidance document, use all electric heat pumps or all GAHP.
Additional errors and warnings: |  |  |  |  | Use heat pump with EN14825/14511 based test data as sole means of meeting main hot water demand prohibited.
RESULTS: Part L compliance Renewable Energy Ratio (RER) Adjustment. Applies to New final and New provisional assessments only. BER Assessor must advise the client of any adjustment to RER, and attach details of adjusted RER to Part L compliance report. This section is completed AFTER the above heat pump calculation results are entered in DEAP software.
Total renewable contribution adjustment | #VALUE! |  |  | [kWh] | Automatically calculated by heat pump calculation tool. Used to adjust renewable energy ratio results in DEAP software to reflect impact of backup / exhaust air / preheat / group heating
Total renewables primary energy from DEAP software |  |  |  | [kWh] | Sourced from DEAP: View assessment: Part L (or RER tab in DEAP workbook) |  | Unadjusted RER | #DIV/0!
Total Primary Energy from DEAP software |  |  |  | [kWh] | Sourced from DEAP: View assessment: Part L (or RER tab in DEAP workbook) |  | Adjusted renewable primary energy | #VALUE!
Adjusted Renewable Energy Ratio to be attached to compliance report | 0 |  |  | [kWh/kWh] | Advise client of this adjusted RER and attach adjusted RER calculation to Part L compliance report |  | Adjusted total primary energy | #VALUE!
Results from each of 3 HPs & additional calculations | Heat pump # 1 | Heat pump # 2 | Heat pump # 3 | Units | Tab | Cell (everything to the right of the tab name) | Heat pump 1 formula in text | Remove bracket
HP number | 1 | 2 | 3
Efficiency of space heating heat pump + backup | #VALUE! | 0% | 0% | % | HP_ | #VALUE! | IF(B14"none",0,$HP_1.$B106) | IF(B14"none",0,$HP_1.$B106
Efficiency adjustment factor space heating | 1 | 0 | 0 |  | HP_ | #VALUE! | IF(B14"none",0,$HP_1.$B107) | IF(B14"none",0,$HP_1.$B107
Efficiency of water heating heat pump + backup | #VALUE! | 0% | 0% | % | HP_ | #VALUE! | IF(B15"none",0,$HP_1.$B108) | IF(B15"none",0,$HP_1.$B108
Efficiency adjustment factor water heating | 1 | 0 | 0 |  | HP_ | #VALUE! | IF(B15"none",0,$HP_1.$B109) | IF(B15"none",0,$HP_1.$B109
Space heating renewables adjustment | #VALUE! | 0 | 0 | kWh | HP_ | #VALUE! | IF(B14"none",0,$HP_1.$F127) | IF(B14"none",0,$HP_1.$F127
Water heating renewables adjustment | #VALUE! | 0 | 0 | kWh | HP_ | #VALUE! | IF(B15"none",0,$HP_1.$F128) | IF(B15"none",0,$HP_1.$F128
% space heating provided by heat pump (<100% means backup is needed) | #VALUE! | 0% | 0% | % | HP_ | #VALUE! | IF(B14"none",0,$HP_1.$B115) | IF(B14"none",0,$HP_1.$B115
% water heating provided by heat pump (<100% means backup is needed) | #VALUE! | 0% | 0% | % | HP_ | #VALUE! | IF(B15"none",0,$HP_1.$B116) | IF(B15"none",0,$HP_1.$B116
Water heating test standard | I.S. EN 16147 |  |  | 0 | HP_ | #VALUE! | IF(B15"none","",$HP_1.$B$68) | IF(B15"none","",$HP_1.$B$68
Maximum allowable % for water heating | 100% | 0% | 0% |  | HP_ | #VALUE! | IF(B15"none",0,$HP_1.$I$68) | IF(B15"none",0,$HP_1.$I$68
Error found in HP calculation? | 0 | 0 | 0 |  | HP_ | #VALUE! | IF(AND(B14"none",B15"none"),0,$HP_1.$AN$4) | IF(AND(B14"none",B15"none",0,$HP_1.$AN$4
Maximum allowable % for water heating error?
Backup used for space heating? | #VALUE!
Backup used for water heating? | #VALUE!
Is heat pump electric or gas (GAHP) for space heating | Electricity |  |  |  | HP_ | #VALUE! | IF(B14"none","",$HP_1.G11) | IF(B14"none","",$HP_1.G11
Is heat pump electric or gas (GAHP) for water heating | Electricity |  |  |  | HP_ | #VALUE! | IF(B15"none","",$HP_1.G63) | IF(B15"none","",$HP_1.G63
Is there use of both GAHP and Elec? | ElectricityElectricity | 1 | 0 | 0
Using only one HP to heat water and uses 14825/14511? | FALSE
100% of main water heating by HPs? | FALSE

## HP_1
Assessment of Heat Pump Performance |  |  |  |  | Heat Pump # | 1 | [6 empty] | I.S. EN 14825 | Yes | Space heating | HP fuel | Low temperature heat pump | Air to Water | Does Ecodesign apply? | Heat Emission Type | Fuel |  | Fixed Outlet | Yes | Test temps | For HP tab | No Hot Water Store | 3XS | ERROR | 0 | 8 | Water heating energy efficiency, ηwh
Description: | Value: | Unit: | Guidance Notes: | [9 empty] | I.S. EN 12309-6 | No | Same Heat Pump providing Space Heating and Domestic Hot Water | Electricity | Not low temperature heat pump | Brine to Water | Ecodesign applies and/or ecodesign data available | 1 or more Radiators present | Electricity | 2.08 | Variable Outlet | No | Low Temperature | Low | Integral Hot Water Storage | XXS |  | 0 | 16 | Coefficient of Performance, COP
Total heat loss (W/K) taken from DEAP | 0 | W/K | Sourced from DEAP "results" tab (or DEAP workbook Fab tab). This is the sum of heat losses from fabric + ventilation + windows | [9 empty] | I.S. EN 13141 |  | Separate Heat Pump providing Space Heating and Domestic Hot Water | Gas fired (GAHP) |  | Water to Water | Ecodesign doesn't apply and ecodesign data unavailable | Fan Coil Units present (no radiators) | Mains Gas | 1.1 |  |  | Medium Temperature | Medium | Separate Hot Water Storage | XS |  | 0 | 24
Heat Loss Watts | Please complete DEAPEntries tab | Watts | Required Space Heating Capacity at design conditions. | [9 empty] | - |  |  |  |  | Exhaust Air to Water |  | Underfloor heating only | LPG Gas (bottled or bulk) | 1.1 |  |  | High Temperature | High | Integral and separate Hot Water Storage | S |  | 0
Is this Heat Pump part of a Group Heating Scheme | No | [11 empty] | I.S. EN 16147 |  |  |  |  | Direct exchange (DX) |  | Air | Heating Oil | 1.1 |  |  | Very high Temperature | Very high |  | M
Proportion of main space heating provided by this heat pump | 0% | % | [10 empty] | - |  |  |  |  | Air to Air |  |  | Biodiesel from renewable sources only | 1.3 | [5 empty] | L
Floor Area of Dwelling | 0 | m2 | Sourced from DEAP: Building: Floors tab (or Dim tab in DEAP workbook) | 0 | 0 | 0 | [6 empty] | I.S. EN 13203-6 |  |  |  |  | Brine to Air |  |  | Bioethanol from renewable sources only | 1.34 | [5 empty] | XL
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: |  | m2 | Sourced from development design details | #NAME? | #NAME? | #NAME? | [6 empty] | I.S. EN 14825/14511 |  |  |  |  | Water to Air |  |  | House coal/ Anthracite | 1.1 | [5 empty] | XXL
Heat Pump for Space Heating |  | Valid space heat pump type selected. | [10 empty] | Code for Space Heating/ DHW |  |  |  |  | Exhaust Air to Air |  |  | Manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Manufacturer of the installed heat pump(s) |  |  | Is this a Low Temperature Heat Pump? |  |  | Not low temperature heat pump | [6 empty] | 1 | Space Heating served by HP | [6 empty] | Peat | 1.1 | [5 empty] | 4XL
Model of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity | [6 empty] | 1 | Hot Water served by HP | [6 empty] | Wood logs/pellets/chips | 1.1
Type of heat pump | Air to Water |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [6 empty] | TRUE | Same HP for Space and Water Heating | [6 empty] | Solid multi-fuel | 1.1
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section):
Space Heating Test Standard | I.S. EN 14825 |  | . |  |  | Heat pump type:Air to Water
Operation Limit Temperature (TOL) |  | oC | Source from Ecodesign Data |  |  | Electric or GAHP:Electricity
Heating water operating limit temperature (WTOL) |  | oC | Source from Ecodesign Data |  |  | Low temp:Not low temperature heat pump
Annual space heating provided by Heat Pump | 0 | kWh |  |  |  | Ecodesign based stds:Ecodesign applies and/or ecodesign data available
Design Outdoor Temperature | -3 | oC | Based on CIBSE Guide A Section 2
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | oC | Source from Net Space Heat Demand "Required mean internal temperature during heating hours degC"
Heat emission type served by heat pump within the dwelling: ¯ | Select all that apply:
1 or more Radiators | Yes
1 or more Fan Coil Units | No |  | Default Supply Temperature
Underfloor Heating | No |  | 55 | oC | Based on SAP input parameters.
Air used as Emitter (to Air Units) | No
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available |  | oC | WARNING: As design flow temperature is less than default, please ensure that documentary evidence is available to support it | [10 empty] | Note: have deleted Row 31 as this is dealt with in the calcs on heating calc (row 38)
Exponent n, characterising type of emission system | 1.2 |  | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Emitter Temperature Drop | 10 | oC | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Return Temperature at design conditions | -10
No of Hrs per Day Heat Pump in Operation | 8 | hrs | Source from Designer/ Installer sign off sheet, default is DEAP heating schedule which is 8 hrs a day
Cut-out hours | 16
Heat pump fuel primary energy factor | 2.08 |  | Depends on whether electric or GAHP
Is a Back Up Space Heater Present within Dwelling | No |  | Source from Designer/ Installer sign off sheet
Back Up Space Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Space Heater | 2.08
Efficiency of Back up Space Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 1
[7 empty] | To air? | Low temp? | Expected selection for each application
Select the test Conditions according to the test data available from I.S. EN 14825 | High Temperature | Yes | Source from Ecodesign Data or accredited tests to I.S. EN 14825 |  |  | GUIDANCE NOTE: High Temperature Application Data is a mandatory requirement under Ecodesign Directive for this heat pump so must be selected as well as any other temperature applications for which test data is available | FALSE | FALSE | Yes
| Low Temperature | No | [6 empty] | No
| Medium Temperature | No | [6 empty] | No
| Very high Temperature | No | [6 empty] | No
| Maximum test temperature allowed for in tests to I.S. EN 14825 | 55
| Test Conditions I.S. EN 14825 | A (88%) -7oC | B (54%) 2oC | C (35%) 7oC | D (15%) 12oC | E* (100%) TOL
Low Temperature Application (35degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W35 | W35 | W35 | W35 | W35
Source from Ecodesign data or I.S. EN14825 Table 8 for air source. Table 12 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Medium Temperature Application (45degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W45 | W45 | W45 | W45 | W45
Source from Ecodesign data or I.S. EN14825 Table 9 for air source. Table 13 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
High Temperature Application (55degC). | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W55 | W55 | W55 | W55 | W55
Source from Ecodesign data or I.S. EN14825 Table 10 for air source. Table 14 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Very high Temperature Application (65degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W65 | W65 | W65 | W65 | W65
Source from Ecodesign data or I.S. EN14825 Table 11 for air source. Table 15 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Heat Pump for Water Heating |  | Valid water heat pump type selected.
Manufacturer of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity
Model of the installed heat pump(s) |  |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [14 empty] | manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Type of heat pump | Air to Water |  | Heat pump fuel primary energy factor (DHW) |  |  | 2.08 | [14 empty] | Peat | 1.1 | [5 empty] | 4XL
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section): | [14 empty] | Wood logs/pellets/chips | 1.1
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water |  | Source from Designer/ Installer sign off sheet or site evidence without Ecodesign |  |  | Heat pump type:Air to Water |  | Max share of hot water by this HP system | Operational temp min this HP | [11 empty] | Solid multi-fuel | 1.1
Water Heating Test Standard | I.S. EN 16147 |  |  |  |  | Electric or GAHP:Electricity |  | 100% | 0
Output from Main Water Heater | 0 | kWh/yr | Source from the Water Heating Tab, Output from Main Water Heater in DEAP |  |  | Ecodesign based stds:Ecodesign applies and/or ecodesign data available
Type of DHW | Separate Hot Water Storage |  | An Integral Hot Water Store forms part of the Heat Pump, refer to DEAP Heat Pump Methodology for guidance.
Cold Water Inlet Temperature | 10 | oC | Based on DEAP Methodology
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | oC | Based on DEAP Methodology and guidelines for prevention of Legionella. Where the store is separate to the heat pump a 5oC drop is assumed.
Volume of DHW Storage | 0 | litres | Sourced from DEAP: Water Heating: options and storage (or WH tab in DEAP workbook) | 0 | 0
Is there a water heater installed as back up for the heat pump | No |  | Source from Designer/ Installer sign off sheet
Back Up Water Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Water Heater | 2.08
Efficiency of Back up Water Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1
Ecodesign based water heating tests to EN16147 (or EN13203-6 for GAHP)*
Source of data | Water heating energy efficiency, ηwh |  | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Water heating energy efficiency, ηwh |  | % | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Equivalent Coefficient of Performance | 0 | kW/kW
Reference Hot Water Temperature |  | oC | Source from Ecodesign Data or accredited tests to EN 16147, set at 40oC if unknown. (or EN13203-6 for GAHP) |  |  | .
Required Source Temperature | 7 | oC | Based on Table 5 of EN 16147 (or EN13203-6 for GAHP)
Capacity of Heat Pump |  | kW | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Declared Load Profile | M |  | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Standby Heat Loss |  | kWh/day | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP), set as 0 if unknown
Volume of DHW accounted for in test |  | litre | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
*May include I.S. EN 14825 / 14511 test data as detailed in guidace document |  |  | #VALUE!
Test Conditions EN 14511-2
Is the Heat Pump Listed on HARP | Yes
Enter SPF based on DEAP Methodology/ HARP | 3.33 | kW/kW | Derive SPF from HARP, certified data COPs in compliance with DEAP methodology or from DEAP table 4a defaults
Is there load or weather compensation present? | Yes |  | Source from Designer/ Installer sign off sheet or site evidence
Does the heat pump have an Integral Immersion | No |  | Source from Designer/ Installer sign off sheet or site evidence
Does heat pump reach a flow temperature of >=65oC | Yes |  | Source from CE marked literature, CE marked dataplates or accredited test data for the heat pump in question.
Test Conditions EN 255-3
Coefficient of Performance | 3.2 | kW/kW | Source from accredited test data certificate
Reference Hot Water Temperature | 54 | oC | Source from accredited test data certificate, set at 40oC if unknown.
Heating Capacity DHW | 7 | kW | Source from accredited test data certificate
Results: See DEAP Entries tab for detail on results for use in DEAP
Results
Efficiency of Main Heating System | #VALUE! | %
Efficiency Adjustment Factor - Main Heating | 1
Efficiency of Main Hot Water System | #VALUE! | %
Efficiency Adjustment Factor - Main Hot Water | 1
% Renewable Contribution from Exhaust Heat Pump for Space Heating | 100% | Only relevant for EAHP |  |  |  | Exhaust Air Flow Rate (m3/hr)
% Renewable Contribution from Exhaust Heat Pump for Water Heating | 100% | Only relevant for EAHP |  |  |  | 0
Is source preheated?
0
% of space heating Provided by Heat Pump | #VALUE! | Space Heating Provided by Heat Pump (not incl backup) | #VALUE! | Efficiency of Space Heat Pump (not incl backup) | #VALUE!
% of Hot Water Provided by Heat Pump | #VALUE! | Water Heating Provided by Heat Pump | #VALUE! | Efficiency of Water Heat Pump (not incl backup) | 0
Calculated environmental energy in this dwelling
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for 14825/ 16147/ 12309-6/ 13206-3 / 13141
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for [14825/14511] /16147/ 12309-6/ 13206-3
Space heating | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
Additional renewable contribution when discounting backup | Adjustment due to backup | Adjustment due to exhaust air | Adjustment for group water heating | Adjustment due to preconditioned heat source | Adjustment to renewable part L contribution | Renewables shown in DEAP | Correct renewable contribution | Check 0
Space heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DEAP Entries Captured Data
Description: | Heat pump # 1 | Heat pump # 2 | Heat pump # 3 | THIS HEAT PUMP |  |  |  | 1 | 2 | 3 | Any | THIS HEAT PUMP
Type of space heating heat pump | Heat Pump | None | None | Heat Pump |  |  | Space Heating served by HP | TRUE | FALSE | FALSE | TRUE | 1
Type of water heating heat pump | Heat Pump | None | None | Heat Pump |  |  | Hot Water served by HP | TRUE | FALSE | FALSE | TRUE | 1
% main space heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
% main water heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
Is heat pump source preconditioned? | No | No | No | No
Is the Heat Pump part of a Group Heating Scheme | No | No | No | No |  |  | Any group heating heat pumps present? | FALSE
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | 0 | 0 | 0
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
Heating calc | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Space Heating Energy Requirement | 0 | #VALUE! | #VALUE! | 0 | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H60
Total Delivered Energy Required (this will be gas or elec) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H69
SPF - Heat Pump & Back up Heater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H71
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H73
Space Heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H75
SPF - Heat Pump only | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H77
Renewable Contribution provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H79
Renewable Contribution from Exhaust Air Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H82
% renewables | 100% | #VALUE! | #VALUE! | 100% | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H85
Hot water
Efficiency for DEAP | 0% | #VALUE! | #VALUE! | 0% | $DHWCalc_ | #VALUE! | $DHWCalc_1.B12
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B17
DHW Demand for Dwelling | 0 | #VALUE! | #VALUE! | 0 | $DHWCalc_ | #VALUE! | $DHWCalc_1.B19
Total Fuel Required for Water Heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B28
SPF | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B30
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B32
Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B34
% Renewable | 100% | #VALUE! | #VALUE! | 100% | $DHWCalc_ | #VALUE! | $DHWCalc_1.B36
SPF | #DIV/0! | #VALUE! | #VALUE! | #DIV/0! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B57
SPF | 333% | #VALUE! | #VALUE! | 333% | $DHWCalc_ | #VALUE! | $DHWCalc_1.B75
Error - Test | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.U14
Error - Dwelling | 1 | #VALUE! | #VALUE! | 1 | $DHWCalc_ | #VALUE! | $DHWCalc_1.V14
Test error text | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | #VALUE! | #VALUE! | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | $DHWCalc_ | #VALUE! | $DHWCalc_1.U16
Dwelling error text | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency. | #VALUE! | #VALUE! | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency. | $DHWCalc_ | #VALUE! | $DHWCalc_1.V16
Space standards ID
Valid space heat pump type selected text | Valid space heat pump type selected. | #VALUE! | #VALUE! | Valid space heat pump type selected. | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A31
Heat pump type: | Air to Water | #VALUE! | #VALUE! | Air to Water | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.B31
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | Electricity | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.C31
Low temp: | Not low temperature heat pump | #VALUE! | #VALUE! | Not low temperature heat pump | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.D31
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | Ecodesign applies and/or ecodesign data available | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.E31
Valid standard chosen? | I.S. EN 14825 | #VALUE! | #VALUE! | I.S. EN 14825 | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.K31
Water standards ID
Valid space heat pump type selected text | Valid water heat pump type selected. | #VALUE! | #VALUE! | Valid water heat pump type selected. | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.A17
Heat pump type: | Air to Water | #VALUE! | #VALUE! | Air to Water | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.B16
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | Electricity | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.C16
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | Ecodesign applies and/or ecodesign data available | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.D16
Valid standard chosen? | I.S. EN 16147 I.S. EN 14825/14511 | #VALUE! | #VALUE! | I.S. EN 16147 I.S. EN 14825/14511 | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.J16
Note on N4: I.S. EN 14511 removed for standalone tool.
Note on N6: I.S. EN 255-3 removed from standalone tool
Note on AD1: These need to be modified once DEAP4 is ready for this change to low, intermediate, medium, high (latest EN14825 nomenclature for temps has changed)

## HP_2
Assessment of Heat Pump Performance |  |  |  |  | Heat Pump # | 2 | [6 empty] | I.S. EN 14825 | Yes | Space heating | HP fuel | Low temperature heat pump | Air to Water | Does Ecodesign apply? | Heat Emission Type | Fuel |  | Fixed Outlet | Yes | Test temps | For HP tab | No Hot Water Store | 3XS | ERROR | 0 | 8 | Water heating energy efficiency, ηwh
Description: | Value: | Unit: | Guidance Notes: | [9 empty] | I.S. EN 12309-6 | No | Same Heat Pump providing Space Heating and Domestic Hot Water | Electricity | Not low temperature heat pump | Brine to Water | Ecodesign applies and/or ecodesign data available | 1 or more Radiators present | Electricity | 2.08 | Variable Outlet | No | Low Temperature | Low | Integral Hot Water Storage | XXS |  | 0 | 16 | Coefficient of Performance, COP
Total heat loss (W/K) taken from DEAP | 0 | W/K | Sourced from DEAP "results" tab (or DEAP workbook Fab tab). This is the sum of heat losses from fabric + ventilation + windows | [9 empty] | I.S. EN 13141 |  | Separate Heat Pump providing Space Heating and Domestic Hot Water | Gas fired (GAHP) |  | Water to Water | Ecodesign doesn't apply and ecodesign data unavailable | Fan Coil Units present (no radiators) | Mains Gas | 1.1 |  |  | Medium Temperature | Medium | Separate Hot Water Storage | XS |  | 0 | 24
Heat Loss Watts | Please complete DEAPEntries tab | Watts | Required Space Heating Capacity at design conditions. | [9 empty] | - |  |  |  |  | Exhaust Air to Water |  | Underfloor heating only | LPG Gas (bottled or bulk) | 1.1 |  |  | High Temperature | High | Integral and separate Hot Water Storage | S |  | 0
Is this Heat Pump part of a Group Heating Scheme | No | [11 empty] | I.S. EN 16147 |  |  |  |  | Direct exchange (DX) |  | Air | Heating Oil | 1.1 |  |  | Very high Temperature | Very high |  | M
Proportion of main space heating provided by this heat pump | 0% | % | [10 empty] | - |  |  |  |  | Air to Air |  |  | Biodiesel from renewable sources only | 1.3 | [5 empty] | L
Floor Area of Dwelling | 0 | m2 | Sourced from DEAP: Building: Floors tab (or Dim tab in DEAP workbook) | 0 | 0 | 0 | [6 empty] | I.S. EN 13203-6 |  |  |  |  | Brine to Air |  |  | Bioethanol from renewable sources only | 1.34 | [5 empty] | XL
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: |  | m2 | Sourced from development design details | #NAME? | #NAME? | #NAME? | [6 empty] | I.S. EN 14825/14511 |  |  |  |  | Water to Air |  |  | House coal/ Anthracite | 1.1 | [5 empty] | XXL
No heat Pump for Space Heating - PROCEED TO WATER HEATING |  | . | [10 empty] | Code for Space Heating/ DHW |  |  |  |  | Exhaust Air to Air |  |  | Manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Manufacturer of the installed heat pump(s) |  |  | Is this a Low Temperature Heat Pump? |  |  | Not low temperature heat pump | [6 empty] | 0 | Space Heating served by HP | [6 empty] | Peat | 1.1 | [5 empty] | 4XL
Model of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity | [6 empty] | 0 | Hot Water served by HP | [6 empty] | Wood logs/pellets/chips | 1.1
Type of heat pump | Air to Water |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [6 empty] | FALSE | Same HP for Space and Water Heating | [6 empty] | Solid multi-fuel | 1.1
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section):
Space Heating Test Standard | I.S. EN 14825 |  | . |  |  | #VALUE!
Operation Limit Temperature (TOL) |  | oC | Source from Ecodesign Data |  |  | #VALUE!
Heating water operating limit temperature (WTOL) |  | oC | Source from Ecodesign Data |  |  | #VALUE!
Annual space heating provided by Heat Pump | 0 | kWh |  |  |  | #VALUE!
Design Outdoor Temperature | -3 | oC | Based on CIBSE Guide A Section 2
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | oC | Source from Net Space Heat Demand "Required mean internal temperature during heating hours degC"
Heat emission type served by heat pump within the dwelling: ¯ | Select all that apply:
1 or more Radiators | Yes
1 or more Fan Coil Units | No |  | Default Supply Temperature
Underfloor Heating | No |  | 55 | oC | Based on SAP input parameters.
Air used as Emitter (to Air Units) | No
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available |  | oC | WARNING: As design flow temperature is less than default, please ensure that documentary evidence is available to support it | [10 empty] | Note: have deleted Row 31 as this is dealt with in the calcs on heating calc (row 38)
Exponent n, characterising type of emission system | 1.2 |  | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Emitter Temperature Drop | 10 | oC | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Return Temperature at design conditions | -10
No of Hrs per Day Heat Pump in Operation | 8 | hrs | Source from Designer/ Installer sign off sheet, default is DEAP heating schedule which is 8 hrs a day
Cut-out hours | 16
Heat pump fuel primary energy factor | 2.08 |  | Depends on whether electric or GAHP
Is a Back Up Space Heater Present within Dwelling | No |  | Source from Designer/ Installer sign off sheet
Back Up Space Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Space Heater | 2.08
Efficiency of Back up Space Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 1
[7 empty] | To air? | Low temp? | Expected selection for each application
Select the test Conditions according to the test data available from I.S. EN 14825 | High Temperature | Yes | Source from Ecodesign Data or accredited tests to I.S. EN 14825 |  |  | GUIDANCE NOTE: High Temperature Application Data is a mandatory requirement under Ecodesign Directive for this heat pump so must be selected as well as any other temperature applications for which test data is available | FALSE | FALSE | Yes
| Low Temperature | No | [6 empty] | No
| Medium Temperature | No | [6 empty] | No
| Very high Temperature | No | [6 empty] | No
| Maximum test temperature allowed for in tests to I.S. EN 14825 | 55
| Test Conditions I.S. EN 14825 | A (88%) -7oC | B (54%) 2oC | C (35%) 7oC | D (15%) 12oC | E* (100%) TOL
Low Temperature Application (35degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W35 | W35 | W35 | W35 | W35
Source from Ecodesign data or I.S. EN14825 Table 8 for air source. Table 12 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Medium Temperature Application (45degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W45 | W45 | W45 | W45 | W45
Source from Ecodesign data or I.S. EN14825 Table 9 for air source. Table 13 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
High Temperature Application (55degC). | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W55 | W55 | W55 | W55 | W55
Source from Ecodesign data or I.S. EN14825 Table 10 for air source. Table 14 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Very high Temperature Application (65degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W65 | W65 | W65 | W65 | W65
Source from Ecodesign data or I.S. EN14825 Table 11 for air source. Table 15 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
No heat Pump for Water Heating - PROCEED TO SPACE HEATING |  | .
Manufacturer of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity
Model of the installed heat pump(s) |  |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [14 empty] | manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Type of heat pump | Air to Water |  | Heat pump fuel primary energy factor (DHW) |  |  | 2.08 | [14 empty] | Peat | 1.1 | [5 empty] | 4XL
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section): | [14 empty] | Wood logs/pellets/chips | 1.1
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water |  | Source from Designer/ Installer sign off sheet or site evidence without Ecodesign |  |  | #VALUE! |  | Max share of hot water by this HP system | Operational temp min this HP | [11 empty] | Solid multi-fuel | 1.1
Water Heating Test Standard | I.S. EN 16147 |  |  |  |  | #VALUE! |  | 100% | 0
Output from Main Water Heater | 0 | kWh/yr | Source from the Water Heating Tab, Output from Main Water Heater in DEAP |  |  | #VALUE!
Type of DHW | Separate Hot Water Storage |  | An Integral Hot Water Store forms part of the Heat Pump, refer to DEAP Heat Pump Methodology for guidance.
Cold Water Inlet Temperature | 10 | oC | Based on DEAP Methodology
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | oC | Based on DEAP Methodology and guidelines for prevention of Legionella. Where the store is separate to the heat pump a 5oC drop is assumed.
Volume of DHW Storage | 0 | litres | Sourced from DEAP: Water Heating: options and storage (or WH tab in DEAP workbook) | 0 | 0
Is there a water heater installed as back up for the heat pump | No |  | Source from Designer/ Installer sign off sheet
Back Up Water Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Water Heater | 2.08
Efficiency of Back up Water Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1
Ecodesign based water heating tests to EN16147 (or EN13203-6 for GAHP)*
Source of data | Water heating energy efficiency, ηwh |  | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Water heating energy efficiency, ηwh |  | % | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Equivalent Coefficient of Performance | 0 | kW/kW
Reference Hot Water Temperature |  | oC | Source from Ecodesign Data or accredited tests to EN 16147, set at 40oC if unknown. (or EN13203-6 for GAHP) |  |  | .
Required Source Temperature | 7 | oC | Based on Table 5 of EN 16147 (or EN13203-6 for GAHP)
Capacity of Heat Pump |  | kW | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Declared Load Profile | M |  | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Standby Heat Loss |  | kWh/day | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP), set as 0 if unknown
Volume of DHW accounted for in test |  | litre | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
*May include I.S. EN 14825 / 14511 test data as detailed in guidace document |  |  | #VALUE!
Test Conditions EN 14511-2
Is the Heat Pump Listed on HARP | Yes
Enter SPF based on DEAP Methodology/ HARP | 3.33 | kW/kW | Derive SPF from HARP, certified data COPs in compliance with DEAP methodology or from DEAP table 4a defaults
Is there load or weather compensation present? | Yes |  | Source from Designer/ Installer sign off sheet or site evidence
Does the heat pump have an Integral Immersion | No |  | Source from Designer/ Installer sign off sheet or site evidence
Does heat pump reach a flow temperature of >=65oC | Yes |  | Source from CE marked literature, CE marked dataplates or accredited test data for the heat pump in question.
Test Conditions EN 255-3
Coefficient of Performance | 3.2 | kW/kW | Source from accredited test data certificate
Reference Hot Water Temperature | 54 | oC | Source from accredited test data certificate, set at 40oC if unknown.
Heating Capacity DHW | 7 | kW | Source from accredited test data certificate
Results: See DEAP Entries tab for detail on results for use in DEAP
Results
Efficiency of Main Heating System | #VALUE! | %
Efficiency Adjustment Factor - Main Heating | 1
Efficiency of Main Hot Water System | #VALUE! | %
Efficiency Adjustment Factor - Main Hot Water | 1
% Renewable Contribution from Exhaust Heat Pump for Space Heating | #VALUE! | Only relevant for EAHP |  |  |  | Exhaust Air Flow Rate (m3/hr)
% Renewable Contribution from Exhaust Heat Pump for Water Heating | #VALUE! | Only relevant for EAHP |  |  |  | 0
Is source preheated?
0
% of space heating Provided by Heat Pump | #VALUE! | Space Heating Provided by Heat Pump (not incl backup) | #VALUE! | Efficiency of Space Heat Pump (not incl backup) | #VALUE!
% of Hot Water Provided by Heat Pump | #VALUE! | Water Heating Provided by Heat Pump | #VALUE! | Efficiency of Water Heat Pump (not incl backup) | #VALUE!
Calculated environmental energy in this dwelling
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for 14825/ 16147/ 12309-6/ 13206-3 / 13141
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for [14825/14511] /16147/ 12309-6/ 13206-3
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Additional renewable contribution when discounting backup | Adjustment due to backup | Adjustment due to exhaust air | Adjustment for group water heating | Adjustment due to preconditioned heat source | Adjustment to renewable part L contribution | Renewables shown in DEAP | Correct renewable contribution | Check 0
Space heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DEAP Entries Captured Data
Description: | Heat pump # 1 | Heat pump # 2 | Heat pump # 3 | THIS HEAT PUMP |  |  |  | 1 | 2 | 3 | Any | THIS HEAT PUMP
Type of space heating heat pump | Heat Pump | None | None | None |  |  | Space Heating served by HP | TRUE | FALSE | FALSE | TRUE | 0
Type of water heating heat pump | Heat Pump | None | None | None |  |  | Hot Water served by HP | TRUE | FALSE | FALSE | TRUE | 0
% main space heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
% main water heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
Is heat pump source preconditioned? | No | No | No | No
Is the Heat Pump part of a Group Heating Scheme | No | No | No | No |  |  | Any group heating heat pumps present? | FALSE
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | 0 | 0 | 0
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
Heating calc | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Space Heating Energy Requirement | 0 | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H60
Total Delivered Energy Required (this will be gas or elec) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H69
SPF - Heat Pump & Back up Heater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H71
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H73
Space Heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H75
SPF - Heat Pump only | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H77
Renewable Contribution provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H79
Renewable Contribution from Exhaust Air Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H82
% renewables | 100% | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H85
Hot water
Efficiency for DEAP | 0% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B12
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B17
DHW Demand for Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B19
Total Fuel Required for Water Heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B28
SPF | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B30
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B32
Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B34
% Renewable | 100% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B36
SPF | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B57
SPF | 333% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B75
Error - Test | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.U14
Error - Dwelling | 1 | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.V14
Test error text | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.U16
Dwelling error text | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency. | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.V16
Space standards ID
Valid space heat pump type selected text | Valid space heat pump type selected. | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A31
Heat pump type: | Air to Water | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.B31
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.C31
Low temp: | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.D31
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.E31
Valid standard chosen? | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.K31
Water standards ID
Valid space heat pump type selected text | Valid water heat pump type selected. | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.A17
Heat pump type: | Air to Water | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.B16
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.C16
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.D16
Valid standard chosen? | I.S. EN 16147 I.S. EN 14825/14511 | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.J16
Note on N4: I.S. EN 14511 removed for standalone tool.
Note on N6: I.S. EN 255-3 removed from standalone tool
Note on AD1: These need to be modified once DEAP4 is ready for this change to low, intermediate, medium, high (latest EN14825 nomenclature for temps has changed)

## HP_3
Assessment of Heat Pump Performance |  |  |  |  | Heat Pump # | 3 | [6 empty] | I.S. EN 14825 | Yes | Space heating | HP fuel | Low temperature heat pump | Air to Water | Does Ecodesign apply? | Heat Emission Type | Fuel |  | Fixed Outlet | Yes | Test temps | For HP tab | No Hot Water Store | 3XS | ERROR | 0 | 8 | Water heating energy efficiency, ηwh
Description: | Value: | Unit: | Guidance Notes: | [9 empty] | I.S. EN 12309-6 | No | Same Heat Pump providing Space Heating and Domestic Hot Water | Electricity | Not low temperature heat pump | Brine to Water | Ecodesign applies and/or ecodesign data available | 1 or more Radiators present | Electricity | 2.08 | Variable Outlet | No | Low Temperature | Low | Integral Hot Water Storage | XXS |  | 0 | 16 | Coefficient of Performance, COP
Total heat loss (W/K) taken from DEAP | 0 | W/K | Sourced from DEAP "results" tab (or DEAP workbook Fab tab). This is the sum of heat losses from fabric + ventilation + windows | [9 empty] | I.S. EN 13141 |  | Separate Heat Pump providing Space Heating and Domestic Hot Water | Gas fired (GAHP) |  | Water to Water | Ecodesign doesn't apply and ecodesign data unavailable | Fan Coil Units present (no radiators) | Mains Gas | 1.1 |  |  | Medium Temperature | Medium | Separate Hot Water Storage | XS |  | 0 | 24
Heat Loss Watts | Please complete DEAPEntries tab | Watts | Required Space Heating Capacity at design conditions. | [9 empty] | - |  |  |  |  | Exhaust Air to Water |  | Underfloor heating only | LPG Gas (bottled or bulk) | 1.1 |  |  | High Temperature | High | Integral and separate Hot Water Storage | S |  | 0
Is this Heat Pump part of a Group Heating Scheme | No | [11 empty] | I.S. EN 16147 |  |  |  |  | Direct exchange (DX) |  | Air | Heating Oil | 1.1 |  |  | Very high Temperature | Very high |  | M
Proportion of main space heating provided by this heat pump | 0% | % | [10 empty] | - |  |  |  |  | Air to Air |  |  | Biodiesel from renewable sources only | 1.3 | [5 empty] | L
Floor Area of Dwelling | 0 | m2 | Sourced from DEAP: Building: Floors tab (or Dim tab in DEAP workbook) | 0 | 0 | 0 | [6 empty] | I.S. EN 13203-6 |  |  |  |  | Brine to Air |  |  | Bioethanol from renewable sources only | 1.34 | [5 empty] | XL
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: |  | m2 | Sourced from development design details | #NAME? | #NAME? | #NAME? | [6 empty] | I.S. EN 14825/14511 |  |  |  |  | Water to Air |  |  | House coal/ Anthracite | 1.1 | [5 empty] | XXL
No heat Pump for Space Heating - PROCEED TO WATER HEATING |  | . | [10 empty] | Code for Space Heating/ DHW |  |  |  |  | Exhaust Air to Air |  |  | Manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Manufacturer of the installed heat pump(s) |  |  | Is this a Low Temperature Heat Pump? |  |  | Not low temperature heat pump | [6 empty] | 0 | Space Heating served by HP | [6 empty] | Peat | 1.1 | [5 empty] | 4XL
Model of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity | [6 empty] | 0 | Hot Water served by HP | [6 empty] | Wood logs/pellets/chips | 1.1
Type of heat pump | Air to Water |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [6 empty] | FALSE | Same HP for Space and Water Heating | [6 empty] | Solid multi-fuel | 1.1
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section):
Space Heating Test Standard | I.S. EN 14825 |  | . |  |  | #VALUE!
Operation Limit Temperature (TOL) |  | oC | Source from Ecodesign Data |  |  | #VALUE!
Heating water operating limit temperature (WTOL) |  | oC | Source from Ecodesign Data |  |  | #VALUE!
Annual space heating provided by Heat Pump | 0 | kWh |  |  |  | #VALUE!
Design Outdoor Temperature | -3 | oC | Based on CIBSE Guide A Section 2
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | oC | Source from Net Space Heat Demand "Required mean internal temperature during heating hours degC"
Heat emission type served by heat pump within the dwelling: ¯ | Select all that apply:
1 or more Radiators | Yes
1 or more Fan Coil Units | No |  | Default Supply Temperature
Underfloor Heating | No |  | 55 | oC | Based on SAP input parameters.
Air used as Emitter (to Air Units) | No
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available |  | oC | WARNING: As design flow temperature is less than default, please ensure that documentary evidence is available to support it | [10 empty] | Note: have deleted Row 31 as this is dealt with in the calcs on heating calc (row 38)
Exponent n, characterising type of emission system | 1.2 |  | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Emitter Temperature Drop | 10 | oC | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Return Temperature at design conditions | -10
No of Hrs per Day Heat Pump in Operation | 8 | hrs | Source from Designer/ Installer sign off sheet, default is DEAP heating schedule which is 8 hrs a day
Cut-out hours | 16
Heat pump fuel primary energy factor | 2.08 |  | Depends on whether electric or GAHP
Is a Back Up Space Heater Present within Dwelling | No |  | Source from Designer/ Installer sign off sheet
Back Up Space Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Space Heater | 2.08
Efficiency of Back up Space Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 1
[7 empty] | To air? | Low temp? | Expected selection for each application
Select the test Conditions according to the test data available from I.S. EN 14825 | High Temperature | Yes | Source from Ecodesign Data or accredited tests to I.S. EN 14825 |  |  | GUIDANCE NOTE: High Temperature Application Data is a mandatory requirement under Ecodesign Directive for this heat pump so must be selected as well as any other temperature applications for which test data is available | FALSE | FALSE | Yes
| Low Temperature | No | [6 empty] | No
| Medium Temperature | No | [6 empty] | No
| Very high Temperature | No | [6 empty] | No
| Maximum test temperature allowed for in tests to I.S. EN 14825 | 55
| Test Conditions I.S. EN 14825 | A (88%) -7oC | B (54%) 2oC | C (35%) 7oC | D (15%) 12oC | E* (100%) TOL
Low Temperature Application (35degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W35 | W35 | W35 | W35 | W35
Source from Ecodesign data or I.S. EN14825 Table 8 for air source. Table 12 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Medium Temperature Application (45degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W45 | W45 | W45 | W45 | W45
Source from Ecodesign data or I.S. EN14825 Table 9 for air source. Table 13 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
High Temperature Application (55degC). | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W55 | W55 | W55 | W55 | W55
Source from Ecodesign data or I.S. EN14825 Table 10 for air source. Table 14 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
Very high Temperature Application (65degC) | Source | A-7 | A2 | A7 | A12 | A
Standard: I.S. EN 14825 | Sink | W65 | W65 | W65 | W65 | W65
Source from Ecodesign data or I.S. EN14825 Table 11 for air source. Table 15 for brine, water or DX source. [These table # references are from 2016 version of this standard] | Heating Capacity (kW)
Coefficient of Performance (kW/kW)
No heat Pump for Water Heating - PROCEED TO SPACE HEATING |  | .
Manufacturer of the installed heat pump(s) |  |  | Is this heat pump electric or gas (GAHP)? |  |  | Electricity
Model of the installed heat pump(s) |  |  | What is the status of this heat pump regarding Ecodesign data? |  |  | Ecodesign applies and/or ecodesign data available | [14 empty] | manufactured smokeless fuel | 1.2 | [5 empty] | 3XL
Type of heat pump | Air to Water |  | Heat pump fuel primary energy factor (DHW) |  |  | 2.08 | [14 empty] | Peat | 1.1 | [5 empty] | 4XL
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet |  | Source from Ecodesign Data |  |  | Diagnostics data in grey cells below showing summary of selections (these will be #NA if invalid options were selected in this section): | [14 empty] | Wood logs/pellets/chips | 1.1
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water |  | Source from Designer/ Installer sign off sheet or site evidence without Ecodesign |  |  | #VALUE! |  | Max share of hot water by this HP system | Operational temp min this HP | [11 empty] | Solid multi-fuel | 1.1
Water Heating Test Standard | I.S. EN 16147 |  |  |  |  | #VALUE! |  | 100% | 0
Output from Main Water Heater | 0 | kWh/yr | Source from the Water Heating Tab, Output from Main Water Heater in DEAP |  |  | #VALUE!
Type of DHW | Separate Hot Water Storage |  | An Integral Hot Water Store forms part of the Heat Pump, refer to DEAP Heat Pump Methodology for guidance.
Cold Water Inlet Temperature | 10 | oC | Based on DEAP Methodology
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | oC | Based on DEAP Methodology and guidelines for prevention of Legionella. Where the store is separate to the heat pump a 5oC drop is assumed.
Volume of DHW Storage | 0 | litres | Sourced from DEAP: Water Heating: options and storage (or WH tab in DEAP workbook) | 0 | 0
Is there a water heater installed as back up for the heat pump | No |  | Source from Designer/ Installer sign off sheet
Back Up Water Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Water Heater | 2.08
Efficiency of Back up Water Heater |  | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1
Ecodesign based water heating tests to EN16147 (or EN13203-6 for GAHP)*
Source of data | Water heating energy efficiency, ηwh |  | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Water heating energy efficiency, ηwh |  | % | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Equivalent Coefficient of Performance | 0 | kW/kW
Reference Hot Water Temperature |  | oC | Source from Ecodesign Data or accredited tests to EN 16147, set at 40oC if unknown. (or EN13203-6 for GAHP) |  |  | .
Required Source Temperature | 7 | oC | Based on Table 5 of EN 16147 (or EN13203-6 for GAHP)
Capacity of Heat Pump |  | kW | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Declared Load Profile | M |  | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
Standby Heat Loss |  | kWh/day | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP), set as 0 if unknown
Volume of DHW accounted for in test |  | litre | Source from Ecodesign Data or accredited tests to EN 16147 (or EN13203-6 for GAHP)
*May include I.S. EN 14825 / 14511 test data as detailed in guidace document |  |  | #VALUE!
Test Conditions EN 14511-2
Is the Heat Pump Listed on HARP | Yes
Enter SPF based on DEAP Methodology/ HARP | 3.33 | kW/kW | Derive SPF from HARP, certified data COPs in compliance with DEAP methodology or from DEAP table 4a defaults
Is there load or weather compensation present? | Yes |  | Source from Designer/ Installer sign off sheet or site evidence
Does the heat pump have an Integral Immersion | No |  | Source from Designer/ Installer sign off sheet or site evidence
Does heat pump reach a flow temperature of >=65oC | Yes |  | Source from CE marked literature, CE marked dataplates or accredited test data for the heat pump in question.
Test Conditions EN 255-3
Coefficient of Performance | 3.2 | kW/kW | Source from accredited test data certificate
Reference Hot Water Temperature | 54 | oC | Source from accredited test data certificate, set at 40oC if unknown.
Heating Capacity DHW | 7 | kW | Source from accredited test data certificate
Results: See DEAP Entries tab for detail on results for use in DEAP
Results
Efficiency of Main Heating System | #VALUE! | %
Efficiency Adjustment Factor - Main Heating | 1
Efficiency of Main Hot Water System | #VALUE! | %
Efficiency Adjustment Factor - Main Hot Water | 1
% Renewable Contribution from Exhaust Heat Pump for Space Heating | #VALUE! | Only relevant for EAHP |  |  |  | Exhaust Air Flow Rate (m3/hr)
% Renewable Contribution from Exhaust Heat Pump for Water Heating | #VALUE! | Only relevant for EAHP |  |  |  | 0
Is source preheated?
0
% of space heating Provided by Heat Pump | #VALUE! | Space Heating Provided by Heat Pump (not incl backup) | #VALUE! | Efficiency of Space Heat Pump (not incl backup) | #VALUE!
% of Hot Water Provided by Heat Pump | #VALUE! | Water Heating Provided by Heat Pump | #VALUE! | Efficiency of Water Heat Pump (not incl backup) | #VALUE!
Calculated environmental energy in this dwelling
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for 14825/ 16147/ 12309-6/ 13206-3 / 13141
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | Heat Use | Fuel usage (elec or gas) | Environmental | check 0 for [14825/14511] /16147/ 12309-6/ 13206-3
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Additional renewable contribution when discounting backup | Adjustment due to backup | Adjustment due to exhaust air | Adjustment for group water heating | Adjustment due to preconditioned heat source | Adjustment to renewable part L contribution | Renewables shown in DEAP | Correct renewable contribution | Check 0
Space heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Water heating | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DEAP Entries Captured Data
Description: | Heat pump # 1 | Heat pump # 2 | Heat pump # 3 | THIS HEAT PUMP |  |  |  | 1 | 2 | 3 | Any | THIS HEAT PUMP
Type of space heating heat pump | Heat Pump | None | None | None |  |  | Space Heating served by HP | TRUE | FALSE | FALSE | TRUE | 0
Type of water heating heat pump | Heat Pump | None | None | None |  |  | Hot Water served by HP | TRUE | FALSE | FALSE | TRUE | 0
% main space heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
% main water heat provided by each heat pump based on system design | 0 | 0 | 0 | 0
Is heat pump source preconditioned? | No | No | No | No
Is the Heat Pump part of a Group Heating Scheme | No | No | No | No |  |  | Any group heating heat pumps present? | FALSE
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | 0 | 0 | 0
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
Heating calc | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Space Heating Energy Requirement | 0 | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H60
Total Delivered Energy Required (this will be gas or elec) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H69
SPF - Heat Pump & Back up Heater | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H71
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H73
Space Heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H75
SPF - Heat Pump only | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H77
Renewable Contribution provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H79
Renewable Contribution from Exhaust Air Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H82
% renewables | 100% | #VALUE! | #VALUE! | #VALUE! | $HeatingCalc_ | #VALUE! | $HeatingCalc_1.H85
Hot water
Efficiency for DEAP | 0% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B12
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B17
DHW Demand for Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B19
Total Fuel Required for Water Heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B28
SPF | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B30
Renewable Contribution calculated in DEAP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B32
Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B34
% Renewable | 100% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B36
SPF | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B57
SPF | 333% | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.B75
Error - Test | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.U14
Error - Dwelling | 1 | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.V14
Test error text | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.U16
Dwelling error text | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency. | #VALUE! | #VALUE! | #VALUE! | $DHWCalc_ | #VALUE! | $DHWCalc_1.V16
Space standards ID
Valid space heat pump type selected text | Valid space heat pump type selected. | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A31
Heat pump type: | Air to Water | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.B31
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.C31
Low temp: | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.D31
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.E31
Valid standard chosen? | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.K31
Water standards ID
Valid space heat pump type selected text | Valid water heat pump type selected. | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.A17
Heat pump type: | Air to Water | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.B16
Electric or GAHP: | Electricity | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.C16
Ecodesign based stds: | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.D16
Valid standard chosen? | I.S. EN 16147 I.S. EN 14825/14511 | #VALUE! | #VALUE! | #VALUE! | $WaterStandardsID_ | #VALUE! | $WaterStandardsID_1.J16
Note on N4: I.S. EN 14511 removed for standalone tool.
Note on N6: I.S. EN 255-3 removed from standalone tool
Note on AD1: These need to be modified once DEAP4 is ready for this change to low, intermediate, medium, high (latest EN14825 nomenclature for temps has changed)

## HeatingCalc_1
EN 15316 methodology |  | Bin 1 | Bin 2 | Bin 3 | Bin 4 | Bin 5 | Total | Guidance Note | Heat Pump # | 1 |  |  |  | Back Up Heating |  |  |  |  | #VALUE! | 0 | [5 empty] | #VALUE!
Bin Data | I.S. EN 14825 Test Conditions (or EN12309-6 for GAHP or EN13141 is some cases) | (E) 100% | (A) 88% | (B) 54% | (c) 35% | (D)15%
Operating Points (Bin Temperatures) | Test Points |  | -7 | 2 | 7 | 12 |  | Based on standard I.S. EN 14825 |  |  |  | TOL | kW | Outdoor temperature bin (deg C) | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8 | Bin Time (h) | Effective Bin Time (h) | Energy to be produced for SH (kWh) | Energy to be produced for DHW (kWh) | Energy Required from Heat Pump (kWh) | Supply Flow Temp oC…as per SAP | Heating Capacity kW…As per 7.5.1 and MCS Tool* (see below) | Required Running Hours (hr) Section 6.6.3 | Diff between Required Running Hrs and Effective Bin..Section 6.6.3 | SAP Methodology Back Up Heater based on Plant Size Ratio | Energy Required from back up (kWh)…Eqt 40 | Total Back Up Heater |  |  | SAP Methodology - Table N9
Lower Limit (oC ) | Mid Test Points | -12 | #VALUE! | -2.5 | 4.5 | 9.5 |  | For Bin 1, the Lower Limit is the Lowest Outdoor Temperature. See 7.3.1 and Table 15 |  |  |  |  | 0 | -12 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Plant Size Ratio | 24 | 16 | 11
Upper Limit, (oC ) | Mid Test Points | #VALUE! | -2.5 | 4.5 | 9.5 | 35 |  | For Bin 5, the Upper Limit is the Upper Outdoor Temperature. See 7.3.1 and Table 15 | [5 empty] | -11 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.2 | 0.4 | 0.53 | 0.64
Source Temperature (oC) | Depends on heat pump type |  | -7 | 2 | 7 | 12 | [7 empty] | -10 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.25 | 0.28 | 0.43 | 0.57
Weighting Factor SH | EN 15316-4-2 Eqt 55 | 0 | 0.005882 | 0.30194 | 0.46292 | 0.22926 | 1 | [6 empty] | -9 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.3 | 0.19 | 0.34 | 0.49
Space Heating Energy (kWh) | Eqt 56 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | -8 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.35 | 0.12 | 0.27 | 0.42
Bin Time (h) | Eqt 57 | 0 | 18 | 1247 | 2933 | 4562 | 8760 | [6 empty] | -7 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.4 | 0.06 | 0.2 | 0.35
Effective Bin Time (h) | Eqt 58 | 0 | 6 | 415.6667 | 977.6667 | 1520.6667 | 2920 | [6 empty] | -6 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.45 | 0.03 | 0.14 | 0.29
Weighting Factor DHW | Eqt 59 | 0 | 0.0020548 | 0.14235 | 0.33482 | 0.52078 | 1 | [6 empty] | -5 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.5 | 0.01 | 0.09 | 0.24
DHW Energy (kWh) | Eqt 60 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | -4 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.55 | 0 | 0.06 | 0.19
[14 empty] | -3 | 0.0013629 | 0.00045662 | 4 | 1.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.6 | 0 | 0.03 | 0.15
Test Data |  |  | -7 | 2 | 7 | 12 | [7 empty] | -2 | 0.0045191 | 0.0015982 | 14 | 4.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.65 | 0 | 0.02 | 0.11
Low Temperature (oC) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 | [7 empty] | -1 | 0.013414 | 0.0050228 | 44 | 14.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.7 | 0 | 0.01 | 0.09
Medium Temperature (oC) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0.032136 | 0.012785 | 112 | 37.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.75 | 0 | 0 | 0.05
High Temperature (oC) | Based on test data according to I.S. EN 14825 | 55 | 55 | 55 | 55 | 55 |  | This is irrelevant for low temp heat pumps but required otherwise | [5 empty] | 1 | 0.039273 | 0.016667 | 146 | 48.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.8 | 0 | 0 | 0.05
Very high Temperature (oC) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2 | 0.055736 | 0.025342 | 222 | 74 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.85 | 0 | 0 | 0.03
Low Temperature COP (kW/kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet COP | [5 empty] | 3 | 0.075301 | 0.036872 | 323 | 107.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.9 | 0 | 0 | 0.02
Medium Temperature COP (kW/kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet COP | [5 empty] | 4 | 0.086079 | 0.045662 | 400 | 133.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.95 | 0 | 0 | 0.01
High Temperature COP (kW/kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet COP | [5 empty] | 5 | 0.087979 | 0.050913 | 446 | 148.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1 | 0 | 0 | 0.01
Very high Temperature COP (kW/kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet COP | [5 empty] | 6 | 0.097735 | 0.062215 | 545 | 181.6667 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1.05 | 0 | 0 | 0
Low Temperature Heating Capacity (kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Capacity | [5 empty] | 7 | 0.097323 | 0.068836 | 603 | 201 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Medium Temperature Heating Capacity (kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Capacity | [5 empty] | 8 | 0.0944 | 0.075114 | 658 | 219.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE! | #VALUE!
High Temperature Heating Capacity (kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Capacity | [5 empty] | 9 | 0.085487 | 0.07774 | 681 | 227 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Very high Temperature Heating Capacity (kW) | Based on test data according to I.S. EN 14825 | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Capacity | [5 empty] | 10 | 0.068755 | 0.072945 | 639 | 213 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Bin -> | E | A | B | C | D | [7 empty] | 11 | 0.059179 | 0.075342 | 660 | 220 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Appropriate Test Data | Lower Test Points | High | [11 empty] | 12 | 0.043757 | 0.069635 | 610 | 203.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Higher Test Points | Error | [11 empty] | 13 | 0.031311 | 0.066438 | 582 | 194 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| To Air Heat Pump | No | [11 empty] | 14 | 0.017252 | 0.054909 | 481 | 160.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Lower Test Points - sink temperature (oC) | High | 55 | 55 | 55 | 55 | 55 | [7 empty] | 15 | 0.0090024 | 0.057306 | 502 | 167.3333 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Higher Test Points - sink temperature (oC ) | Error | 0 | 0 | 0 | 0 | 0 | [7 empty] | 16 |  | 0.043721 | 383 | 127.6667 |  | 0 | 0
Lower Test Points - COP (kWh/kWh) | High | 0 | 0 | 0 | 0 | 0 | [7 empty] | 17 |  | 0.029566 | 259 | 86.3333 |  | 0 | 0
Higher Test Points - COP (kWh/kWh) | Error | 0 | 0 | 0 | 0 | 0 |  | Supply flow temp in "single test point" case = | [5 empty] | 18 |  | 0.019406 | 170 | 56.6667 |  | 0 | 0
Lower Test Points - Heating Capacity (kW) | High | 0 | 0 | 0 | 0 | 0 |  | 55 | [5 empty] | 19 |  | 0.012785 | 112 | 37.3333 |  | 0 | 0
Higher Test Points - Heating Capacity (kW) | Error | 0 | 0 | 0 | 0 | 0 | [7 empty] | 20 |  | 0.0076484 | 67 | 22.3333 |  | 0 | 0 |  | * Interpolation equation as per EN 15316, however using same methodology as MCS tool as single point data may ony be available
Supply Flow Temperature based on Single Test Points | As per SAP approach - Based on 55oC only (or 35oC for low temperature heat pumps) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | 55degC basis for Supply Flow Temperature to meet the mandatory test points in Ecodesign, to use for single test point data | [5 empty] | 21 |  | 0.0042237 | 37 | 12.3333 |  | 0 | 0
Source Temperature | Section F2.1 (2008 version of 15316-4-2, not provided in 15316-4-2:2017 or associated standards) |  | -7 | 2 | 7 | 12 |  | Source temp depends on source being air, water, brine, exhaust air, DX | [5 empty] | 22 |  | 0.0030822 | 27 | 9 |  | 0 | 0
Supply Flow Temperature | As per SAP approach in 2016 and 2012 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 23 |  | 0.0022831 | 20 | 6.6667 |  | 0 | 0
Heating Capacity for Source Temp | Section 7.5.1 | Not applicable, for water and exhaust heat pumps the source temperature is constant, for air heat pumps we have test data at various conditions and for brine/DX heat pumps as we don't have different source temperatures it is not possible to carry out interpolation. | [11 empty] | 24 |  | 0.001484 | 13 | 4.3333 |  | 0 | 0
Heating Capacity for Supply Temp | Linear Interpolation (Section 7.5.1) | 0 | 0 | 0 | 0 | 0 |  | Refer to Heating Capacity calculated for each external temperature as per Column W. Note: As per Annex D, heating capacity cannot be adjusted for single test points | [5 empty] | 25 |  | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 26 |  | 0 | 0 | 0 |  | 0 | 0
Standard Rating Conditions | Based on EN 14511 | 0 | kW |  |  |  |  | In EN 14825, the water flow rate is determined according to EN 14511 at standard rating conditions. Similar approach for GAHP using standard rating conditions from EN12309. Updated 1st half 2019 as identified in consultation document | DeltaT | Tout |  |  |  | 27 |  | 0 | 0 | 0 |  | 0 | 0
Mass Flow Rate | kg/s, Equation D.7 | 0 | [5 empty] | DeltaT is based on EN14511 for electrically driven heat pumps and EN12309 for GAHP, 4.182 kJ/kg/K is the specific heat capacity of water. Also accounts for "to air" systems as (5 x 4.182 degree delta T ≈ 1.2*(35-RoomTemp)) | 5 | 55 |  |  |  | 28 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Lower Temp | oC, Equation D.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [7 empty] | 29 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Higher Temp | oC, Equation D.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [7 empty] | 30 |  | 0 | 0 | 0 |  | 0 | 0
Required Heating Capacity at design conditions | Taken from DEAP | #VALUE! | kW |  |  |  |  | PSR | #VALUE! |  |  |  |  | 31 |  | 0 | 0 | 0 |  | 0 | 0
Delta T for emitter | Taken from Input | 10 | [11 empty] | 32 |  | 0 | 0 | 0 |  | 0 | 0
Required Mass flow at design conditions | kg/s, Equation D.7 | #VALUE! | [11 empty] | 33 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Lower Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 34 |  | 0 | 0 | 0 |  | 0 | 0
Temp Spread at Higher Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 35 |  | 0 | 0 | 0 |  | 0 | 0
Correction Factor COP Lower Temp Test Points | eqt D.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
Correction Factor COP Higher Temp Test Points | eqt D.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
COP corrected for Lower Temp | eqt D.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
COP corrected for Higher Temp | eqt D.8 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Interpolation of COP | Linear Interpolation refer to Eqt D4 Single Point | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | For Single set of test points, the COP is based on adjustment in Annex D & eqt D.4 and is based on Supply Temp of 55oC (or 35oC for low temperature heat pumps), to meet the mandatory test results for Ecodesign. As outlined in Annex D, accuracy deteriorates with increasing distance from test points therefore methodology not used for Fixed Outlet. Updated 1st half 2019 to fix case where Avoiding negative COPs in interpolation formula....as identified in public consultation document
Storage Losses |  | Buffer Vessels for space heating only excluded, as per other systems in DEAP
Space Heating Energy Requirement | kWh | 0 | 0 | 0 | 0 | 0 | 0
Energy to be produced by back up heater for Space Heating only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy Provided by Backup Space Heater for Space Heating Only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | This has been converted to equivalent energy in the same fuel as the heat pump using Bivalent system
Back Up for Temperature Increase not included as test data for higher temperatures must be provided.
Auxiliary Energy for central heating pumps & DHW pumps excluded as allowed for in DEAP
Recoverable heat from auxiliary energy (pumps) and thermal losses (storage) excluded as allowed for in DEAP
Delivered fuel (gas or elec) for Space Heating from heat pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Delivered Energy Required (this will be gas or elec) | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump & Back up Heater | [6 empty] | #VALUE!
Renewable Contribution calculated in DEAP | [6 empty] | #VALUE! | kWh
Space Heating Provided by Heat Pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump only | [6 empty] | #VALUE!
Renewable Contribution provided by Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
% Renewable |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Renewable Contribution from Exhaust Air Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
[7 empty] | 100% | % renewables
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | Please complete DEAPEntries tab | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | 0% | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | Air to Water | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | Fixed Outlet | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | I.S. EN 14825 | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! |  | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! |  | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | -3 | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | Please complete DEAP Entries tab | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | 1.2 | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | 10 | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | -10 | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | 8 | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | 16 | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | 2.08 | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | 2.08 | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | 100% | $HP_ | #VALUE! | $HP_1.B36
Test temps: temp1 | Low Temperature | #VALUE! | #VALUE! | Low Temperature | $HP_ | #VALUE! | $HP_1.$AD2
Test temps: temp2 | Medium Temperature | #VALUE! | #VALUE! | Medium Temperature | $HP_ | #VALUE! | $HP_1.$AD3
Test temps: temp3 | High Temperature | #VALUE! | #VALUE! | High Temperature | $HP_ | #VALUE! | $HP_1.$AD4
Test temps: temp4 | Very high Temperature | #VALUE! | #VALUE! | Very high Temperature | $HP_ | #VALUE! | $HP_1.$AD5
For HP tab: temp1 | Low | #VALUE! | #VALUE! | Low | $HP_ | #VALUE! | $HP_1.$AE2
For HP tab: temp2 | Medium | #VALUE! | #VALUE! | Medium | $HP_ | #VALUE! | $HP_1.$AE3
For HP tab: temp3 | High | #VALUE! | #VALUE! | High | $HP_ | #VALUE! | $HP_1.$AE4
For HP tab: temp4 | Very high | #VALUE! | #VALUE! | Very high | $HP_ | #VALUE! | $HP_1.$AE5
High Temperature | Yes | #VALUE! | #VALUE! | Yes | $HP_ | #VALUE! | $HP_1.C38
Low Temperature | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.C39
Medium Temperature | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.C40
Very high Temperature | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.C41
Maximum test temperature allowed for in tests to I.S. EN 14825 | 55 | #VALUE! | #VALUE! | 55 | $HP_ | #VALUE! | $HP_1.C42
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | Not low temperature heat pump | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | Ecodesign applies and/or ecodesign data available | $HP_ | #VALUE! | $HP_1.G12
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B69
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.G112
Cdh placeholderLow Temperature | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
Cdh placeholderMedium Temperature | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
Cdh placeholderHigh Temperature | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
Cdh placeholderVery high Temperature | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | placeholder | #N/A | #N/A | #N/A
| HP identifier: | This HP | This HP | This HP | This HP | This HP | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | Heat pump 1 source cell name as text |  |  |  |  | Tab |  |  |  |  | Cell (everything to the right of the tab name)
| Bin | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E
COP and heating capacity | Bin: HP identifier:Bin->; A: 1A; B: 1B; C: 1C; D: 1D; E: 1E; A: 1A; B: 1B; C: 1C; D: 1D; E: 1E; A: 2A; B: 2B; C: 2C; D: 2D; E: 2E; A: 3A; B: 3B; C: 3C; D: 3D; E: 3E
Low Temperature COP (kW/kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C47 | $HP_1.D47 | $HP_1.E47 | $HP_1.F47 | $HP_1.G47 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Medium Temperature COP (kW/kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C51 | $HP_1.D51 | $HP_1.E51 | $HP_1.F51 | $HP_1.G51 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
High Temperature COP (kW/kW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C55 | $HP_1.D55 | $HP_1.E55 | $HP_1.F55 | $HP_1.G55 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Very high Temperature COP (kW/kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C59 | $HP_1.D59 | $HP_1.E59 | $HP_1.F59 | $HP_1.G59 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Low Temperature Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C46 | $HP_1.D46 | $HP_1.E46 | $HP_1.F46 | $HP_1.G46 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Medium Temperature Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C50 | $HP_1.D50 | $HP_1.E50 | $HP_1.F50 | $HP_1.G50 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
High Temperature Heating Capacity (kW) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C54 | $HP_1.D54 | $HP_1.E54 | $HP_1.F54 | $HP_1.G54 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Very high Temperature Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C58 | $HP_1.D58 | $HP_1.E58 | $HP_1.F58 | $HP_1.G58 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## HeatingCalc_2
EN 15316 methodology |  | Bin 1 | Bin 2 | Bin 3 | Bin 4 | Bin 5 | Total | Guidance Note | Heat Pump # | 2 |  |  |  | Back Up Heating |  |  |  |  | #VALUE! | #VALUE! | [5 empty] | #VALUE!
Bin Data | I.S. EN 14825 Test Conditions (or EN12309-6 for GAHP or EN13141 is some cases) | (E) 100% | (A) 88% | (B) 54% | (c) 35% | (D)15%
Operating Points (Bin Temperatures) | Test Points | #VALUE! | -7 | 2 | 7 | 12 |  | #VALUE! |  |  |  | TOL | kW | Outdoor temperature bin (deg C) | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8 | Bin Time (h) | Effective Bin Time (h) | Energy to be produced for SH (kWh) | Energy to be produced for DHW (kWh) | Energy Required from Heat Pump (kWh) | Supply Flow Temp oC…as per SAP | Heating Capacity kW…As per 7.5.1 and MCS Tool* (see below) | Required Running Hours (hr) Section 6.6.3 | Diff between Required Running Hrs and Effective Bin..Section 6.6.3 | SAP Methodology Back Up Heater based on Plant Size Ratio | Energy Required from back up (kWh)…Eqt 40 | Total Back Up Heater |  |  | SAP Methodology - Table N9
Lower Limit (oC ) | Mid Test Points | -12 | #VALUE! | -2.5 | 4.5 | 9.5 |  | For Bin 1, the Lower Limit is the Lowest Outdoor Temperature. See 7.3.1 and Table 15 |  |  |  | #VALUE! | #VALUE! | -12 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Plant Size Ratio | 24 | 16 | 11
Upper Limit, (oC ) | Mid Test Points | #VALUE! | -2.5 | 4.5 | 9.5 | 35 |  | For Bin 5, the Upper Limit is the Upper Outdoor Temperature. See 7.3.1 and Table 15 | [5 empty] | -11 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.2 | 0.4 | 0.53 | 0.64
Source Temperature (oC) | Depends on heat pump type | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | -10 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.25 | 0.28 | 0.43 | 0.57
Weighting Factor SH | EN 15316-4-2 Eqt 55 | 0 | 0.005882 | 0.30194 | 0.46292 | 0.22926 | 1 | [6 empty] | -9 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.3 | 0.19 | 0.34 | 0.49
Space Heating Energy (kWh) | Eqt 56 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -8 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.35 | 0.12 | 0.27 | 0.42
Bin Time (h) | Eqt 57 | 0 | 18 | 1247 | 2933 | 4562 | 8760 | [6 empty] | -7 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.4 | 0.06 | 0.2 | 0.35
Effective Bin Time (h) | Eqt 58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -6 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.45 | 0.03 | 0.14 | 0.29
Weighting Factor DHW | Eqt 59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -5 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.5 | 0.01 | 0.09 | 0.24
DHW Energy (kWh) | Eqt 60 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -4 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.55 | 0 | 0.06 | 0.19
[14 empty] | -3 | 0.0013629 | 0.00045662 | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.6 | 0 | 0.03 | 0.15
Test Data |  | #VALUE! | -7 | 2 | 7 | 12 | [7 empty] | -2 | 0.0045191 | 0.0015982 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.65 | 0 | 0.02 | 0.11
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | -1 | 0.013414 | 0.0050228 | 44 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.7 | 0 | 0.01 | 0.09
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 0 | 0.032136 | 0.012785 | 112 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.75 | 0 | 0 | 0.05
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | This is irrelevant for low temp heat pumps but required otherwise | [5 empty] | 1 | 0.039273 | 0.016667 | 146 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.8 | 0 | 0 | 0.05
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 2 | 0.055736 | 0.025342 | 222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.85 | 0 | 0 | 0.03
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 3 | 0.075301 | 0.036872 | 323 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.9 | 0 | 0 | 0.02
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 4 | 0.086079 | 0.045662 | 400 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.95 | 0 | 0 | 0.01
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 5 | 0.087979 | 0.050913 | 446 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1 | 0 | 0 | 0.01
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 6 | 0.097735 | 0.062215 | 545 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1.05 | 0 | 0 | 0
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 7 | 0.097323 | 0.068836 | 603 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 8 | 0.0944 | 0.075114 | 658 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 9 | 0.085487 | 0.07774 | 681 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 10 | 0.068755 | 0.072945 | 639 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Bin -> | E | A | B | C | D | [7 empty] | 11 | 0.059179 | 0.075342 | 660 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Appropriate Test Data | Lower Test Points | #VALUE! | [11 empty] | 12 | 0.043757 | 0.069635 | 610 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Higher Test Points | #VALUE! | [11 empty] | 13 | 0.031311 | 0.066438 | 582 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| To Air Heat Pump | #VALUE! | [11 empty] | 14 | 0.017252 | 0.054909 | 481 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Lower Test Points - sink temperature (oC) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 15 | 0.0090024 | 0.057306 | 502 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Higher Test Points - sink temperature (oC ) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 16 |  | 0.043721 | 383 | #VALUE! |  | #VALUE! | #VALUE!
Lower Test Points - COP (kWh/kWh) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 17 |  | 0.029566 | 259 | #VALUE! |  | #VALUE! | #VALUE!
Higher Test Points - COP (kWh/kWh) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Supply flow temp in "single test point" case = | [5 empty] | 18 |  | 0.019406 | 170 | #VALUE! |  | #VALUE! | #VALUE!
Lower Test Points - Heating Capacity (kW) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | [5 empty] | 19 |  | 0.012785 | 112 | #VALUE! |  | #VALUE! | #VALUE!
Higher Test Points - Heating Capacity (kW) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 20 |  | 0.0076484 | 67 | #VALUE! |  | #VALUE! | #VALUE! |  | * Interpolation equation as per EN 15316, however using same methodology as MCS tool as single point data may ony be available
Supply Flow Temperature based on Single Test Points | As per SAP approach - Based on 55oC only (or 35oC for low temperature heat pumps) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | [5 empty] | 21 |  | 0.0042237 | 37 | #VALUE! |  | #VALUE! | #VALUE!
Source Temperature | Section F2.1 (2008 version of 15316-4-2, not provided in 15316-4-2:2017 or associated standards) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Source temp depends on source being air, water, brine, exhaust air, DX | [5 empty] | 22 |  | 0.0030822 | 27 | #VALUE! |  | #VALUE! | #VALUE!
Supply Flow Temperature | As per SAP approach in 2016 and 2012 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 23 |  | 0.0022831 | 20 | #VALUE! |  | #VALUE! | #VALUE!
Heating Capacity for Source Temp | Section 7.5.1 | Not applicable, for water and exhaust heat pumps the source temperature is constant, for air heat pumps we have test data at various conditions and for brine/DX heat pumps as we don't have different source temperatures it is not possible to carry out interpolation. | [11 empty] | 24 |  | 0.001484 | 13 | #VALUE! |  | #VALUE! | #VALUE!
Heating Capacity for Supply Temp | Linear Interpolation (Section 7.5.1) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Refer to Heating Capacity calculated for each external temperature as per Column W. Note: As per Annex D, heating capacity cannot be adjusted for single test points | [5 empty] | 25 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
[14 empty] | 26 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Standard Rating Conditions | Based on EN 14511 | #VALUE! | kW |  |  |  |  | In EN 14825, the water flow rate is determined according to EN 14511 at standard rating conditions. Similar approach for GAHP using standard rating conditions from EN12309. Updated 1st half 2019 as identified in consultation document | DeltaT | Tout |  |  |  | 27 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Mass Flow Rate | kg/s, Equation D.7 | #VALUE! | [5 empty] | DeltaT is based on EN14511 for electrically driven heat pumps and EN12309 for GAHP, 4.182 kJ/kg/K is the specific heat capacity of water. Also accounts for "to air" systems as (5 x 4.182 degree delta T ≈ 1.2*(35-RoomTemp)) | #VALUE! | #VALUE! |  |  |  | 28 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 29 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 30 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Required Heating Capacity at design conditions | Taken from DEAP | #VALUE! | kW |  |  |  |  | PSR | #VALUE! |  |  |  |  | 31 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Delta T for emitter | Taken from Input | #VALUE! | [11 empty] | 32 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Required Mass flow at design conditions | kg/s, Equation D.7 | #VALUE! | [11 empty] | 33 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 34 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 35 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Correction Factor COP Lower Temp Test Points | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
Correction Factor COP Higher Temp Test Points | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
COP corrected for Lower Temp | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
COP corrected for Higher Temp | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Interpolation of COP | Linear Interpolation refer to Eqt D4 Single Point | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | For Single set of test points, the COP is based on adjustment in Annex D & eqt D.4 and is based on Supply Temp of 55oC (or 35oC for low temperature heat pumps), to meet the mandatory test results for Ecodesign. As outlined in Annex D, accuracy deteriorates with increasing distance from test points therefore methodology not used for Fixed Outlet. Updated 1st half 2019 to fix case where Avoiding negative COPs in interpolation formula....as identified in public consultation document
Storage Losses |  | Buffer Vessels for space heating only excluded, as per other systems in DEAP
Space Heating Energy Requirement | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy to be produced by back up heater for Space Heating only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy Provided by Backup Space Heater for Space Heating Only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | This has been converted to equivalent energy in the same fuel as the heat pump using Bivalent system
Back Up for Temperature Increase not included as test data for higher temperatures must be provided.
Auxiliary Energy for central heating pumps & DHW pumps excluded as allowed for in DEAP
Recoverable heat from auxiliary energy (pumps) and thermal losses (storage) excluded as allowed for in DEAP
Delivered fuel (gas or elec) for Space Heating from heat pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Delivered Energy Required (this will be gas or elec) | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump & Back up Heater | [6 empty] | #VALUE!
Renewable Contribution calculated in DEAP | [6 empty] | #VALUE! | kWh
Space Heating Provided by Heat Pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump only | [6 empty] | #VALUE!
Renewable Contribution provided by Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
% Renewable |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Renewable Contribution from Exhaust Air Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
[7 empty] | #VALUE! | % renewables
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B36
Test temps: temp1 | Low Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD2
Test temps: temp2 | Medium Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD3
Test temps: temp3 | High Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD4
Test temps: temp4 | Very high Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD5
For HP tab: temp1 | Low | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE2
For HP tab: temp2 | Medium | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE3
For HP tab: temp3 | High | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE4
For HP tab: temp4 | Very high | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE5
High Temperature | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C38
Low Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C39
Medium Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C40
Very high Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C41
Maximum test temperature allowed for in tests to I.S. EN 14825 | 55 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C42
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G12
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B69
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G112
Cdh placeholderLow Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderMedium Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderHigh Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderVery high Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HP identifier: | This HP | This HP | This HP | This HP | This HP | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | Heat pump 1 source cell name as text |  |  |  |  | Tab |  |  |  |  | Cell (everything to the right of the tab name)
| Bin | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E
COP and heating capacity | Bin: HP identifier:Bin->; A: 2A; B: 2B; C: 2C; D: 2D; E: 2E; A: 1A; B: 1B; C: 1C; D: 1D; E: 1E; A: 2A; B: 2B; C: 2C; D: 2D; E: 2E; A: 3A; B: 3B; C: 3C; D: 3D; E: 3E
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C47 | $HP_1.D47 | $HP_1.E47 | $HP_1.F47 | $HP_1.G47 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C51 | $HP_1.D51 | $HP_1.E51 | $HP_1.F51 | $HP_1.G51 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C55 | $HP_1.D55 | $HP_1.E55 | $HP_1.F55 | $HP_1.G55 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C59 | $HP_1.D59 | $HP_1.E59 | $HP_1.F59 | $HP_1.G59 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C46 | $HP_1.D46 | $HP_1.E46 | $HP_1.F46 | $HP_1.G46 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C50 | $HP_1.D50 | $HP_1.E50 | $HP_1.F50 | $HP_1.G50 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C54 | $HP_1.D54 | $HP_1.E54 | $HP_1.F54 | $HP_1.G54 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C58 | $HP_1.D58 | $HP_1.E58 | $HP_1.F58 | $HP_1.G58 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## HeatingCalc_3
EN 15316 methodology |  | Bin 1 | Bin 2 | Bin 3 | Bin 4 | Bin 5 | Total | Guidance Note | Heat Pump # | 3 |  |  |  | Back Up Heating |  |  |  |  | #VALUE! | #VALUE! | [5 empty] | #VALUE!
Bin Data | I.S. EN 14825 Test Conditions (or EN12309-6 for GAHP or EN13141 is some cases) | (E) 100% | (A) 88% | (B) 54% | (c) 35% | (D)15%
Operating Points (Bin Temperatures) | Test Points | #VALUE! | -7 | 2 | 7 | 12 |  | #VALUE! |  |  |  | TOL | kW | Outdoor temperature bin (deg C) | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8 | Bin Time (h) | Effective Bin Time (h) | Energy to be produced for SH (kWh) | Energy to be produced for DHW (kWh) | Energy Required from Heat Pump (kWh) | Supply Flow Temp oC…as per SAP | Heating Capacity kW…As per 7.5.1 and MCS Tool* (see below) | Required Running Hours (hr) Section 6.6.3 | Diff between Required Running Hrs and Effective Bin..Section 6.6.3 | SAP Methodology Back Up Heater based on Plant Size Ratio | Energy Required from back up (kWh)…Eqt 40 | Total Back Up Heater |  |  | SAP Methodology - Table N9
Lower Limit (oC ) | Mid Test Points | -12 | #VALUE! | -2.5 | 4.5 | 9.5 |  | For Bin 1, the Lower Limit is the Lowest Outdoor Temperature. See 7.3.1 and Table 15 |  |  |  | #VALUE! | #VALUE! | -12 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Plant Size Ratio | 24 | 16 | 11
Upper Limit, (oC ) | Mid Test Points | #VALUE! | -2.5 | 4.5 | 9.5 | 35 |  | For Bin 5, the Upper Limit is the Upper Outdoor Temperature. See 7.3.1 and Table 15 | [5 empty] | -11 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.2 | 0.4 | 0.53 | 0.64
Source Temperature (oC) | Depends on heat pump type | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | -10 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.25 | 0.28 | 0.43 | 0.57
Weighting Factor SH | EN 15316-4-2 Eqt 55 | 0 | 0.005882 | 0.30194 | 0.46292 | 0.22926 | 1 | [6 empty] | -9 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.3 | 0.19 | 0.34 | 0.49
Space Heating Energy (kWh) | Eqt 56 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -8 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.35 | 0.12 | 0.27 | 0.42
Bin Time (h) | Eqt 57 | 0 | 18 | 1247 | 2933 | 4562 | 8760 | [6 empty] | -7 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.4 | 0.06 | 0.2 | 0.35
Effective Bin Time (h) | Eqt 58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -6 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.45 | 0.03 | 0.14 | 0.29
Weighting Factor DHW | Eqt 59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -5 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.5 | 0.01 | 0.09 | 0.24
DHW Energy (kWh) | Eqt 60 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [6 empty] | -4 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.55 | 0 | 0.06 | 0.19
[14 empty] | -3 | 0.0013629 | 0.00045662 | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.6 | 0 | 0.03 | 0.15
Test Data |  | #VALUE! | -7 | 2 | 7 | 12 | [7 empty] | -2 | 0.0045191 | 0.0015982 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.65 | 0 | 0.02 | 0.11
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | -1 | 0.013414 | 0.0050228 | 44 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.7 | 0 | 0.01 | 0.09
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 0 | 0.032136 | 0.012785 | 112 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.75 | 0 | 0 | 0.05
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | This is irrelevant for low temp heat pumps but required otherwise | [5 empty] | 1 | 0.039273 | 0.016667 | 146 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.8 | 0 | 0 | 0.05
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 2 | 0.055736 | 0.025342 | 222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.85 | 0 | 0 | 0.03
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 3 | 0.075301 | 0.036872 | 323 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.9 | 0 | 0 | 0.02
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 4 | 0.086079 | 0.045662 | 400 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 0.95 | 0 | 0 | 0.01
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 5 | 0.087979 | 0.050913 | 446 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1 | 0 | 0 | 0.01
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet COP | [5 empty] | 6 | 0.097735 | 0.062215 | 545 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 1.05 | 0 | 0 | 0
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 7 | 0.097323 | 0.068836 | 603 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 8 | 0.0944 | 0.075114 | 658 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 9 | 0.085487 | 0.07774 | 681 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Taken from Input Sheet Capacity | [5 empty] | 10 | 0.068755 | 0.072945 | 639 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Bin -> | E | A | B | C | D | [7 empty] | 11 | 0.059179 | 0.075342 | 660 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Appropriate Test Data | Lower Test Points | #VALUE! | [11 empty] | 12 | 0.043757 | 0.069635 | 610 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Higher Test Points | #VALUE! | [11 empty] | 13 | 0.031311 | 0.066438 | 582 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| To Air Heat Pump | #VALUE! | [11 empty] | 14 | 0.017252 | 0.054909 | 481 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Lower Test Points - sink temperature (oC) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 15 | 0.0090024 | 0.057306 | 502 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Higher Test Points - sink temperature (oC ) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 16 |  | 0.043721 | 383 | #VALUE! |  | #VALUE! | #VALUE!
Lower Test Points - COP (kWh/kWh) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 17 |  | 0.029566 | 259 | #VALUE! |  | #VALUE! | #VALUE!
Higher Test Points - COP (kWh/kWh) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Supply flow temp in "single test point" case = | [5 empty] | 18 |  | 0.019406 | 170 | #VALUE! |  | #VALUE! | #VALUE!
Lower Test Points - Heating Capacity (kW) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | [5 empty] | 19 |  | 0.012785 | 112 | #VALUE! |  | #VALUE! | #VALUE!
Higher Test Points - Heating Capacity (kW) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 20 |  | 0.0076484 | 67 | #VALUE! |  | #VALUE! | #VALUE! |  | * Interpolation equation as per EN 15316, however using same methodology as MCS tool as single point data may ony be available
Supply Flow Temperature based on Single Test Points | As per SAP approach - Based on 55oC only (or 35oC for low temperature heat pumps) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | [5 empty] | 21 |  | 0.0042237 | 37 | #VALUE! |  | #VALUE! | #VALUE!
Source Temperature | Section F2.1 (2008 version of 15316-4-2, not provided in 15316-4-2:2017 or associated standards) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Source temp depends on source being air, water, brine, exhaust air, DX | [5 empty] | 22 |  | 0.0030822 | 27 | #VALUE! |  | #VALUE! | #VALUE!
Supply Flow Temperature | As per SAP approach in 2016 and 2012 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 23 |  | 0.0022831 | 20 | #VALUE! |  | #VALUE! | #VALUE!
Heating Capacity for Source Temp | Section 7.5.1 | Not applicable, for water and exhaust heat pumps the source temperature is constant, for air heat pumps we have test data at various conditions and for brine/DX heat pumps as we don't have different source temperatures it is not possible to carry out interpolation. | [11 empty] | 24 |  | 0.001484 | 13 | #VALUE! |  | #VALUE! | #VALUE!
Heating Capacity for Supply Temp | Linear Interpolation (Section 7.5.1) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Refer to Heating Capacity calculated for each external temperature as per Column W. Note: As per Annex D, heating capacity cannot be adjusted for single test points | [5 empty] | 25 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
[14 empty] | 26 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Standard Rating Conditions | Based on EN 14511 | #VALUE! | kW |  |  |  |  | In EN 14825, the water flow rate is determined according to EN 14511 at standard rating conditions. Similar approach for GAHP using standard rating conditions from EN12309. Updated 1st half 2019 as identified in consultation document | DeltaT | Tout |  |  |  | 27 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Mass Flow Rate | kg/s, Equation D.7 | #VALUE! | [5 empty] | DeltaT is based on EN14511 for electrically driven heat pumps and EN12309 for GAHP, 4.182 kJ/kg/K is the specific heat capacity of water. Also accounts for "to air" systems as (5 x 4.182 degree delta T ≈ 1.2*(35-RoomTemp)) | #VALUE! | #VALUE! |  |  |  | 28 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 29 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 30 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Required Heating Capacity at design conditions | Taken from DEAP | #VALUE! | kW |  |  |  |  | PSR | #VALUE! |  |  |  |  | 31 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Delta T for emitter | Taken from Input | #VALUE! | [11 empty] | 32 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Required Mass flow at design conditions | kg/s, Equation D.7 | #VALUE! | [11 empty] | 33 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 34 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp Test Points at design conditions | oC, Equation D.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [7 empty] | 35 |  | 0 | 0 | #VALUE! |  | #VALUE! | #VALUE!
Correction Factor COP Lower Temp Test Points | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
Correction Factor COP Higher Temp Test Points | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | As per consultation 1st half 2019: The constant values for ΔTsk and ΔTsc 5 (annotated as ϑHP;gen;cond;int(t) and ϑHP;gen;evap;int(t) in the 2017 version of the EN15316-4-2 standard) have increased from 4K to 5K.
COP corrected for Lower Temp | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
COP corrected for Higher Temp | eqt D.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Interpolation of COP | Linear Interpolation refer to Eqt D4 Single Point | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | For Single set of test points, the COP is based on adjustment in Annex D & eqt D.4 and is based on Supply Temp of 55oC (or 35oC for low temperature heat pumps), to meet the mandatory test results for Ecodesign. As outlined in Annex D, accuracy deteriorates with increasing distance from test points therefore methodology not used for Fixed Outlet. Updated 1st half 2019 to fix case where Avoiding negative COPs in interpolation formula....as identified in public consultation document
Storage Losses |  | Buffer Vessels for space heating only excluded, as per other systems in DEAP
Space Heating Energy Requirement | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy to be produced by back up heater for Space Heating only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy Provided by Backup Space Heater for Space Heating Only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | This has been converted to equivalent energy in the same fuel as the heat pump using Bivalent system
Back Up for Temperature Increase not included as test data for higher temperatures must be provided.
Auxiliary Energy for central heating pumps & DHW pumps excluded as allowed for in DEAP
Recoverable heat from auxiliary energy (pumps) and thermal losses (storage) excluded as allowed for in DEAP
Delivered fuel (gas or elec) for Space Heating from heat pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Delivered Energy Required (this will be gas or elec) | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump & Back up Heater | [6 empty] | #VALUE!
Renewable Contribution calculated in DEAP | [6 empty] | #VALUE! | kWh
Space Heating Provided by Heat Pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump only | [6 empty] | #VALUE!
Renewable Contribution provided by Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
% Renewable |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Renewable Contribution from Exhaust Air Heat Pump |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | kWh
[7 empty] | #VALUE! | % renewables
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B36
Test temps: temp1 | Low Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD2
Test temps: temp2 | Medium Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD3
Test temps: temp3 | High Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD4
Test temps: temp4 | Very high Temperature | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AD5
For HP tab: temp1 | Low | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE2
For HP tab: temp2 | Medium | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE3
For HP tab: temp3 | High | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE4
For HP tab: temp4 | Very high | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.$AE5
High Temperature | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C38
Low Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C39
Medium Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C40
Very high Temperature | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C41
Maximum test temperature allowed for in tests to I.S. EN 14825 | 55 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.C42
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G12
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B69
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G112
Cdh placeholderLow Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderMedium Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderHigh Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cdh placeholderVery high Temperature | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
placeholder | placeholder | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HP identifier: | This HP | This HP | This HP | This HP | This HP | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | Heat pump 1 source cell name as text |  |  |  |  | Tab |  |  |  |  | Cell (everything to the right of the tab name)
| Bin | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E | A | B | C | D | E
COP and heating capacity | Bin: HP identifier:Bin->; A: 3A; B: 3B; C: 3C; D: 3D; E: 3E; A: 1A; B: 1B; C: 1C; D: 1D; E: 1E; A: 2A; B: 2B; C: 2C; D: 2D; E: 2E; A: 3A; B: 3B; C: 3C; D: 3D; E: 3E
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C47 | $HP_1.D47 | $HP_1.E47 | $HP_1.F47 | $HP_1.G47 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C51 | $HP_1.D51 | $HP_1.E51 | $HP_1.F51 | $HP_1.G51 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C55 | $HP_1.D55 | $HP_1.E55 | $HP_1.F55 | $HP_1.G55 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C59 | $HP_1.D59 | $HP_1.E59 | $HP_1.F59 | $HP_1.G59 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C46 | $HP_1.D46 | $HP_1.E46 | $HP_1.F46 | $HP_1.G46 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C50 | $HP_1.D50 | $HP_1.E50 | $HP_1.F50 | $HP_1.G50 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C54 | $HP_1.D54 | $HP_1.E54 | $HP_1.F54 | $HP_1.G54 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_1.C58 | $HP_1.D58 | $HP_1.E58 | $HP_1.F58 | $HP_1.G58 | $HP_ | $HP_ | $HP_ | $HP_ | $HP_ | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!

## DHWCalc_1
[8 empty] | Heat Pump # | 1 | From Ecodesign / 814
EN 16147 (or EN13203-6 for GAHP, or 14825 in limited pre-heat cases) | [9 empty] | Tapping Cycle | kWh/day |  | Test Check | Installed Check | Error - Test | Error - Dwelling
Volume of Tank in Test | 0 |  |  | based on test data | [5 empty] | 3XS | 0.345 | 7 |  |  | 0 | 0
Average Storage Temperature | 65 | oC | [7 empty] | XXS | 2.1 | 15 |  |  | 0 | 0
Standby Heat loss | 0 | kWh/day |  | based on test data | [5 empty] | XS | 2.1 | 15 |  |  | 0 | 0
Declared Load Profile | M | [8 empty] | S | 2.1 | 36 |  |  | 0 | 0
Min Volume for cycle | 65 | litre | [7 empty] | M | 5.845 | 65 | #VALUE! | 39 | #VALUE! | 1
DHW Demand based on Cycle | 5.845 | kWh/day |  | based on default for Cycle | [5 empty] | L | 11.655 | 130 | #VALUE! | 78 | 0 | 0
COP based on I.S. EN 16147 | 0 | [8 empty] | XL | 19.07 | 210 | #VALUE! | 126 | 0 | 0
Capacity of Heat Pump | 0 | kW | [7 empty] | XXL | 24.53 | 300 | #VALUE! | 180 | 0 | 0
[10 empty] | 3XL | 46.76 | 520 | #VALUE! | 312 | 0 | 0
Efficiency for DEAP | 0 |  |  | based on equation from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps, converting 15316-4-2 SPF to SAP SPF | [5 empty] | 4XL | 93.52 | 1040 | #VALUE! | 624 | 0 | 0
0
Reference Temperature |  | oC | [12 empty] | #VALUE! | 1
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC | [12 empty] | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency.
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE!
DHW Demand for Dwelling | 0 | kWh
Required Running Hours | #DIV/0! | hrs
Effective Bin Time | 2920 | hrs |  | based on eqt 58 from EN 15316
Difference between Req and Effective | #DIV/0!
Fraction of Demand met by backup to meet operation hours shortfall | #DIV/0!
Heat Pump Electricity/gas | #VALUE! | kWh
Back Up Heater due to temperature shortfall | #VALUE! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Back Up Heater due to operation shortfall | #DIV/0! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Total Fuel Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
% Renewable | 100%
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
EN 255-3
DHW Demand for Dwelling | 0 | kWh
COP based on EN 255 | 3.2
Capacity of Heat Pump | 7 | kW
Reference Temperature | 54 | oC
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC
Fraction of Backup energy due to temperature shortfall | 0.2 |  |  | based on eqt 18 from EN 15316
Electricity required by Heat Pump | 0 | kWh
Electricity required by Back Up Heater | 0 | kWh
Total Electricity Required for Water Heating | 0 | kWh
SPF | #DIV/0!
Renewable Contribution calculated in DEAP | #DIV/0! | kWh
Hot Water Provided by Heat Pump | 0 | kWh
SPF - Heat Pump Only | #DIV/0!
Renewable Contribution provided by Heat Pump | #DIV/0! | kWh
EN 14511
DHW Demand for Dwelling | 0 | kWh
COP based on EN 14511 | 3.33
Efficiency Adjustment Factor | 0.7
SPF | 3.33
Total Electricity Required for Water Heating | 0 | kWh
Renewable Contribution calculated in DEAP | 0 | kWh
Hot Water Provided by Heat Pump | 0 | kWh
Electricity required by Heat Pump | 0 | kWh
Renewable Contribution provided by Heat Pump | 0 | kWh
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | Please complete DEAPEntries tab | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | 0% | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | Air to Water | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | Fixed Outlet | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | I.S. EN 14825 | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! |  | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! |  | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | -3 | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | Please complete DEAP Entries tab | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | 1.2 | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | 10 | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | -10 | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | 8 | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | 16 | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | 2.08 | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | 2.08 | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | 100% | $HP_ | #VALUE! | $HP_1.B36
Type of heat pump | Air to Water | #VALUE! | #VALUE! | Air to Water | $HP_ | #VALUE! | $HP_1.B65
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | Fixed Outlet | $HP_ | #VALUE! | $HP_1.B66
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water | #VALUE! | #VALUE! | Same Heat Pump providing Space Heating and Domestic Hot Water | $HP_ | #VALUE! | $HP_1.B67
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | I.S. EN 16147 | $HP_ | #VALUE! | $HP_1.B68
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B69
Type of DHW | Separate Hot Water Storage | #VALUE! | #VALUE! | Separate Hot Water Storage | $HP_ | #VALUE! | $HP_1.B70
Cold Water Inlet Temperature | 10 | #VALUE! | #VALUE! | 10 | $HP_ | #VALUE! | $HP_1.B71
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | #VALUE! | #VALUE! | 65 | $HP_ | #VALUE! | $HP_1.B72
Volume of DHW Storage | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B73
Is there a water heater installed as back up for the heat pump | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B74
Back Up Water Heater Fuel | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.B75
Primary Energy Factor for Back Up Water Heater | 2.08 | #VALUE! | #VALUE! | 2.08 | $HP_ | #VALUE! | $HP_1.B76
Efficiency of Back up Water Heater | 0 | #VALUE! | #VALUE! | 0% | $HP_ | #VALUE! | $HP_1.B77
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1 | #VALUE! | #VALUE! | 100% | $HP_ | #VALUE! | $HP_1.B78
Source of data | Water heating energy efficiency, ηwh | #VALUE! | #VALUE! | Water heating energy efficiency, ηwh | $HP_ | #VALUE! | $HP_1.B81
Water heating energy efficiency, ηwh | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B82
Equivalent Coefficient of Performance | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B83
Reference Hot Water Temperature |  | #VALUE! | #VALUE! |  | $HP_ | #VALUE! | $HP_1.B84
Required Source Temperature | 7 | #VALUE! | #VALUE! | 7 | $HP_ | #VALUE! | $HP_1.B85
Capacity of Heat Pump | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B86
Declared Load Profile | M | #VALUE! | #VALUE! | M | $HP_ | #VALUE! | $HP_1.B87
Standby Heat Loss | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B88
Volume of DHW accounted for in test | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B89
Is the Heat Pump Listed on HARP | Yes | #VALUE! | #VALUE! | Yes | $HP_ | #VALUE! | $HP_1.B92
Enter SPF based on DEAP Methodology/ HARP | 3.33 | #VALUE! | #VALUE! | 3.33 | $HP_ | #VALUE! | $HP_1.B93
Is there load or weather compensation present? | Yes | #VALUE! | #VALUE! | Yes | $HP_ | #VALUE! | $HP_1.B94
Does the heat pump have an Integral Immersion | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B95
Does heat pump reach a flow temperature of >=65oC | Yes | #VALUE! | #VALUE! | Yes | $HP_ | #VALUE! | $HP_1.B96
Coefficient of Performance | 3.2 | #VALUE! | #VALUE! | 3.2 | $HP_ | #VALUE! | $HP_1.B100
Reference Hot Water Temperature | 54 | #VALUE! | #VALUE! | 54 | $HP_ | #VALUE! | $HP_1.B101
Heating Capacity DHW | 7 | #VALUE! | #VALUE! | 7 | $HP_ | #VALUE! | $HP_1.B102
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B103
Results: See DEAP Entries tab for detail on results for use in DEAP | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B104
Results | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B105
Efficiency of Main Heating System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B106
Efficiency Adjustment Factor - Main Heating | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.B107
Efficiency of Main Hot Water System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B108
Efficiency Adjustment Factor - Main Hot Water | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.B109
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B110
% Renewable Contribution from Exhaust Heat Pump for Space Heating | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.B111
% Renewable Contribution from Exhaust Heat Pump for Water Heating | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.B112
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B113
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B114
% of space heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B115
% of Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B116
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B117
Calculated environmental energy in this dwelling | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B118
0 | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B119
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | Heat Pump Efficiency | $HP_ | #VALUE! | $HP_1.B120
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B121
Water heating | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B122
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | Heat Pump Efficiency | $HP_ | #VALUE! | $HP_1.B123
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B124
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B125
Additional renewable contribution when discounting backup | Adjustment due to backup | #VALUE! | #VALUE! | Adjustment due to backup | $HP_ | #VALUE! | $HP_1.B126
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B127
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B128
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.G112
DEAP Entries Captured Data | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B187
Description: | Heat pump # 1 | #VALUE! | #VALUE! | Heat pump # 1 | $HP_ | #VALUE! | $HP_1.B188
Type of space heating heat pump | Heat Pump | #VALUE! | #VALUE! | Heat Pump | $HP_ | #VALUE! | $HP_1.B189
Type of water heating heat pump | Heat Pump | #VALUE! | #VALUE! | Heat Pump | $HP_ | #VALUE! | $HP_1.B190
% main space heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B191
% main water heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B192
Is heat pump source preconditioned? | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B193
Is the Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | No | $HP_ | #VALUE! | $HP_1.B194
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | #VALUE! | #VALUE! | 0 | $HP_ | #VALUE! | $HP_1.B195

## DHWCalc_2
[8 empty] | Heat Pump # | 2 | From Ecodesign / 814
EN 16147 (or EN13203-6 for GAHP, or 14825 in limited pre-heat cases) | [9 empty] | Tapping Cycle | kWh/day |  | Test Check | Installed Check | Error - Test | Error - Dwelling
Volume of Tank in Test | #VALUE! |  |  | based on test data | [5 empty] | 3XS | 0.345 | 7 |  |  | #VALUE! | #VALUE!
Average Storage Temperature | #VALUE! | oC | [7 empty] | XXS | 2.1 | 15 |  |  | #VALUE! | #VALUE!
Standby Heat loss | #VALUE! | kWh/day |  | based on test data | [5 empty] | XS | 2.1 | 15 |  |  | #VALUE! | #VALUE!
Declared Load Profile | #VALUE! | [8 empty] | S | 2.1 | 36 |  |  | #VALUE! | #VALUE!
Min Volume for cycle | #VALUE! | litre | [7 empty] | M | 5.845 | 65 | #VALUE! | 39 | #VALUE! | #VALUE!
DHW Demand based on Cycle | #VALUE! | kWh/day |  | based on default for Cycle | [5 empty] | L | 11.655 | 130 | #VALUE! | 78 | #VALUE! | #VALUE!
#VALUE! | #VALUE! | [8 empty] | XL | 19.07 | 210 | #VALUE! | 126 | #VALUE! | #VALUE!
Capacity of Heat Pump | #VALUE! | kW | [7 empty] | XXL | 24.53 | 300 | #VALUE! | 180 | #VALUE! | #VALUE!
[10 empty] | 3XL | 46.76 | 520 | #VALUE! | 312 | #VALUE! | #VALUE!
Efficiency for DEAP | #VALUE! |  |  | based on equation from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps, converting 15316-4-2 SPF to SAP SPF | [5 empty] | 4XL | 93.52 | 1040 | #VALUE! | 624 | #VALUE! | #VALUE!
0
Reference Temperature | #VALUE! | oC | [12 empty] | #VALUE! | #VALUE!
Temperature of DHW | #VALUE! | oC
Temperature of Cold Water Inlet | #VALUE! | oC | [12 empty] | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency.
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE!
DHW Demand for Dwelling | #VALUE! | kWh
Required Running Hours | #VALUE! | hrs
Effective Bin Time | #VALUE! | hrs |  | based on eqt 58 from EN 15316
Difference between Req and Effective | #VALUE!
Fraction of Demand met by backup to meet operation hours shortfall | #VALUE!
Heat Pump Electricity/gas | #VALUE! | kWh
Back Up Heater due to temperature shortfall | #VALUE! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Back Up Heater due to operation shortfall | #VALUE! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Total Fuel Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
% Renewable | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
EN 255-3
DHW Demand for Dwelling | #VALUE! | kWh
COP based on EN 255 | #VALUE!
Capacity of Heat Pump | #VALUE! | kW
Reference Temperature | #VALUE! | oC
Temperature of DHW | #VALUE! | oC
Temperature of Cold Water Inlet | #VALUE! | oC
Fraction of Backup energy due to temperature shortfall | #VALUE! |  |  | based on eqt 18 from EN 15316
Electricity required by Heat Pump | #VALUE! | kWh
Electricity required by Back Up Heater | #VALUE! | kWh
Total Electricity Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
SPF - Heat Pump Only | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
EN 14511
DHW Demand for Dwelling | #VALUE! | kWh
COP based on EN 14511 | #VALUE!
Efficiency Adjustment Factor | #VALUE!
SPF | #VALUE!
Total Electricity Required for Water Heating | #VALUE! | kWh
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
Electricity required by Heat Pump | #VALUE! | kWh
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B36
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B65
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B66
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B67
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B69
Type of DHW | Separate Hot Water Storage | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B70
Cold Water Inlet Temperature | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B71
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B72
Volume of DHW Storage | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B73
Is there a water heater installed as back up for the heat pump | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B74
Back Up Water Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B75
Primary Energy Factor for Back Up Water Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B76
Efficiency of Back up Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B77
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B78
Source of data | Water heating energy efficiency, ηwh | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B81
Water heating energy efficiency, ηwh | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B82
Equivalent Coefficient of Performance | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B83
Reference Hot Water Temperature |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B84
Required Source Temperature | 7 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B85
Capacity of Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B86
Declared Load Profile | M | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B87
Standby Heat Loss | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B88
Volume of DHW accounted for in test | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B89
Is the Heat Pump Listed on HARP | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B92
Enter SPF based on DEAP Methodology/ HARP | 3.33 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B93
Is there load or weather compensation present? | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B94
Does the heat pump have an Integral Immersion | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B95
Does heat pump reach a flow temperature of >=65oC | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B96
Coefficient of Performance | 3.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B100
Reference Hot Water Temperature | 54 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B101
Heating Capacity DHW | 7 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B102
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B103
Results: See DEAP Entries tab for detail on results for use in DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B104
Results | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B105
Efficiency of Main Heating System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B106
Efficiency Adjustment Factor - Main Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B107
Efficiency of Main Hot Water System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B108
Efficiency Adjustment Factor - Main Hot Water | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B109
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B110
% Renewable Contribution from Exhaust Heat Pump for Space Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B111
% Renewable Contribution from Exhaust Heat Pump for Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B112
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B113
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B114
% of space heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B115
% of Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B116
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B117
Calculated environmental energy in this dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B118
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B119
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B120
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B121
Water heating | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B122
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B123
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B124
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B125
Additional renewable contribution when discounting backup | Adjustment due to backup | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B126
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B127
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B128
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G112
DEAP Entries Captured Data | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B187
Description: | Heat pump # 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B188
Type of space heating heat pump | Heat Pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B189
Type of water heating heat pump | Heat Pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B190
% main space heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B191
% main water heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B192
Is heat pump source preconditioned? | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B193
Is the Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B194
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B195

## DHWCalc_3
[8 empty] | Heat Pump # | 3 | From Ecodesign / 814
EN 16147 (or EN13203-6 for GAHP, or 14825 in limited pre-heat cases) | [9 empty] | Tapping Cycle | kWh/day |  | Test Check | Installed Check | Error - Test | Error - Dwelling
Volume of Tank in Test | #VALUE! |  |  | based on test data | [5 empty] | 3XS | 0.345 | 7 |  |  | #VALUE! | #VALUE!
Average Storage Temperature | #VALUE! | oC | [7 empty] | XXS | 2.1 | 15 |  |  | #VALUE! | #VALUE!
Standby Heat loss | #VALUE! | kWh/day |  | based on test data | [5 empty] | XS | 2.1 | 15 |  |  | #VALUE! | #VALUE!
Declared Load Profile | #VALUE! | [8 empty] | S | 2.1 | 36 |  |  | #VALUE! | #VALUE!
Min Volume for cycle | #VALUE! | litre | [7 empty] | M | 5.845 | 65 | #VALUE! | 39 | #VALUE! | #VALUE!
DHW Demand based on Cycle | #VALUE! | kWh/day |  | based on default for Cycle | [5 empty] | L | 11.655 | 130 | #VALUE! | 78 | #VALUE! | #VALUE!
#VALUE! | #VALUE! | [8 empty] | XL | 19.07 | 210 | #VALUE! | 126 | #VALUE! | #VALUE!
Capacity of Heat Pump | #VALUE! | kW | [7 empty] | XXL | 24.53 | 300 | #VALUE! | 180 | #VALUE! | #VALUE!
[10 empty] | 3XL | 46.76 | 520 | #VALUE! | 312 | #VALUE! | #VALUE!
Efficiency for DEAP | #VALUE! |  |  | based on equation from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps, converting 15316-4-2 SPF to SAP SPF | [5 empty] | 4XL | 93.52 | 1040 | #VALUE! | 624 | #VALUE! | #VALUE!
0
Reference Temperature | #VALUE! | oC | [12 empty] | #VALUE! | #VALUE!
Temperature of DHW | #VALUE! | oC
Temperature of Cold Water Inlet | #VALUE! | oC | [12 empty] | WARNING: As the test storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | WARNING: As the test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency.
Fraction of Demand met by backup energy to meet temperature shortfall | #VALUE!
DHW Demand for Dwelling | #VALUE! | kWh
Required Running Hours | #VALUE! | hrs
Effective Bin Time | #VALUE! | hrs |  | based on eqt 58 from EN 15316
Difference between Req and Effective | #VALUE!
Fraction of Demand met by backup to meet operation hours shortfall | #VALUE!
Heat Pump Electricity/gas | #VALUE! | kWh
Back Up Heater due to temperature shortfall | #VALUE! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Back Up Heater due to operation shortfall | #VALUE! | kWh |  | Efficiency of Back up Water Heater adjusted relative to fuel type of Heatpump
Total Fuel Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
% Renewable | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
EN 255-3
DHW Demand for Dwelling | #VALUE! | kWh
COP based on EN 255 | #VALUE!
Capacity of Heat Pump | #VALUE! | kW
Reference Temperature | #VALUE! | oC
Temperature of DHW | #VALUE! | oC
Temperature of Cold Water Inlet | #VALUE! | oC
Fraction of Backup energy due to temperature shortfall | #VALUE! |  |  | based on eqt 18 from EN 15316
Electricity required by Heat Pump | #VALUE! | kWh
Electricity required by Back Up Heater | #VALUE! | kWh
Total Electricity Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
SPF - Heat Pump Only | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
EN 14511
DHW Demand for Dwelling | #VALUE! | kWh
COP based on EN 14511 | #VALUE!
Efficiency Adjustment Factor | #VALUE!
SPF | #VALUE!
Total Electricity Required for Water Heating | #VALUE! | kWh
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
Electricity required by Heat Pump | #VALUE! | kWh
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Same HP for Space and Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Total heat loss (W/K) taken from DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B3
Heat Loss Watts | Please complete DEAPEntries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B4
Is this Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B5
Proportion of main space heating provided by this heat pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B6
Floor Area of Dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B7
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B8
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B13
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Operation Limit Temperature (TOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B15
Heating water operating limit temperature (WTOL) |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B16
Annual space heating provided by Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B17
Design Outdoor Temperature | -3 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B18
Indoor Design Temperature (Mean Internal Temperature) | Please complete DEAP Entries tab | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B19
Air used as Emitter (to Air Units) | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B24
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B25
Exponent n, characterising type of emission system | 1.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B26
Emitter Temperature Drop | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B27
Return Temperature at design conditions | -10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B28
No of Hrs per Day Heat Pump in Operation | 8 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B29
Cut-out hours | 16 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B30
Heat pump fuel primary energy factor | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B31
Is a Back Up Space Heater Present within Dwelling | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B32
Back Up Space Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B33
Primary Energy Factor for Back Up Space Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B34
Efficiency of Back up Space Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B35
Adjusted Efficiency of Back up Space Heater relative to fuel used for heat pump | 100% | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B36
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B65
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Fixed Outlet | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B66
Describe the water heating heat pump arrangement | Same Heat Pump providing Space Heating and Domestic Hot Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B67
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Output from Main Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B69
Type of DHW | Separate Hot Water Storage | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B70
Cold Water Inlet Temperature | 10 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B71
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B72
Volume of DHW Storage | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B73
Is there a water heater installed as back up for the heat pump | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B74
Back Up Water Heater Fuel | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B75
Primary Energy Factor for Back Up Water Heater | 2.08 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B76
Efficiency of Back up Water Heater | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B77
Adjusted Efficiency of Back up Water Heater relative to fuel used by heat pump | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B78
Source of data | Water heating energy efficiency, ηwh | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B81
Water heating energy efficiency, ηwh | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B82
Equivalent Coefficient of Performance | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B83
Reference Hot Water Temperature |  | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B84
Required Source Temperature | 7 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B85
Capacity of Heat Pump | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B86
Declared Load Profile | M | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B87
Standby Heat Loss | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B88
Volume of DHW accounted for in test | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B89
Is the Heat Pump Listed on HARP | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B92
Enter SPF based on DEAP Methodology/ HARP | 3.33 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B93
Is there load or weather compensation present? | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B94
Does the heat pump have an Integral Immersion | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B95
Does heat pump reach a flow temperature of >=65oC | Yes | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B96
Coefficient of Performance | 3.2 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B100
Reference Hot Water Temperature | 54 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B101
Heating Capacity DHW | 7 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B102
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B103
Results: See DEAP Entries tab for detail on results for use in DEAP | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B104
Results | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B105
Efficiency of Main Heating System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B106
Efficiency Adjustment Factor - Main Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B107
Efficiency of Main Hot Water System | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B108
Efficiency Adjustment Factor - Main Hot Water | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B109
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B110
% Renewable Contribution from Exhaust Heat Pump for Space Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B111
% Renewable Contribution from Exhaust Heat Pump for Water Heating | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B112
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B113
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B114
% of space heating Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B115
% of Hot Water Provided by Heat Pump | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B116
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B117
Calculated environmental energy in this dwelling | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B118
0 | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B119
Heat pump standalone without backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B120
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B121
Water heating | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B122
Heat pump with backup (not accounting for Exhaust adjustment) | Heat Pump Efficiency | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B123
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B124
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B125
Additional renewable contribution when discounting backup | Adjustment due to backup | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B126
Space heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B127
Water heating | #VALUE! | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B128
Exhaust Air Flow Rate (m3/hr) | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G112
DEAP Entries Captured Data | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B187
Description: | Heat pump # 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B188
Type of space heating heat pump | Heat Pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B189
Type of water heating heat pump | Heat Pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B190
% main space heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B191
% main water heat provided by each heat pump based on system design | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B192
Is heat pump source preconditioned? | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B193
Is the Heat Pump part of a Group Heating Scheme | No | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B194
If "Exhaust Air Heat Pump(s)" what is the total exhaust Air Flow Rate | 0 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B195

## SpaceStandardsID_1
Space heating HP type |  |  |  | Diagnostics cell: Air to Water Electricity Not low temperature heat pump Ecodesign applies and/or ecodesign data available I.S. EN 14825 | Space heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  | Space heating valid standards | Heat Pump # | 1
Selector | Type of heat pump | Electric / Gas(GAHP) | Low temperature | Ecodesign applicable? | I.S. EN 14825 | I.S. EN 14511 | I.S. EN 13141 | I.S. EN 12309-6
1 | Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Brine to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Brine to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Water to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Water to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Exhaust Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Direct exchange (DX) | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Air to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Brine to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Water to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
| Air to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Air to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Brine to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Brine to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Water to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Water to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
| Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Brine to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Water to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 13141 |  | I.S. EN 14511 I.S. EN 13141
| Brine to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Water to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
| Exhaust Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  |  | I.S. EN 13141 |  | I.S. EN 13141
Valid space heat pump type selected. | Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | <-Applicable values -> |  |  |  | I.S. EN 14825
Valid space heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | Air to Water | $HP_ | #VALUE! | $HP_1.B12
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | Not low temperature heat pump | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | Ecodesign applies and/or ecodesign data available | $HP_ | #VALUE! | $HP_1.G12
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | I.S. EN 14825 | $HP_ | #VALUE! | $HP_1.B14
Space Heating served by HP | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N12
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | I.S. EN 16147 | $HP_ | #VALUE! | $HP_1.B68
Note on A31: 1 and only one means a valid heat pump is selected

## SpaceStandardsID_2
Space heating HP type |  |  |  | #VALUE! | Space heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  | Space heating valid standards | Heat Pump # | 2
Selector | Type of heat pump | Electric / Gas(GAHP) | Low temperature | Ecodesign applicable? | I.S. EN 14825 | I.S. EN 14511 | I.S. EN 13141 | I.S. EN 12309-6
#VALUE! | Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Exhaust Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Direct exchange (DX) | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Air to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Water to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Water to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Brine to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Water to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 13141 |  | I.S. EN 14511 I.S. EN 13141
#VALUE! | Brine to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Water to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Exhaust Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  |  | I.S. EN 13141 |  | I.S. EN 13141
#VALUE! | #N/A | #N/A | #N/A | #N/A | <-Applicable values -> |  |  |  | #N/A
#VALUE!
#VALUE!
Valid space heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G12
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Space Heating served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Note on A31: 1 and only one means a valid heat pump is selected

## SpaceStandardsID_3
Space heating HP type |  |  |  | #VALUE! | Space heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  | Space heating valid standards | Heat Pump # | 3
Selector | Type of heat pump | Electric / Gas(GAHP) | Low temperature | Ecodesign applicable? | I.S. EN 14825 | I.S. EN 14511 | I.S. EN 13141 | I.S. EN 12309-6
#VALUE! | Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Exhaust Air to Water | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Direct exchange (DX) | Electricity | Low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Brine to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Water to Air | Electricity | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available | I.S. EN 14825 |  |  |  | I.S. EN 14825
#VALUE! | Air to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Air to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Water to Water | Gas fired (GAHP) | Not low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Water to Water | Gas fired (GAHP) | Low temperature heat pump | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 12309-6 | I.S. EN 12309-6
#VALUE! | Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Brine to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Water to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Exhaust Air to Water | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Direct exchange (DX) | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 13141 |  | I.S. EN 14511 I.S. EN 13141
#VALUE! | Brine to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Water to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  | I.S. EN 14511
#VALUE! | Exhaust Air to Air | Electricity | Not low temperature heat pump | Ecodesign doesn't apply and ecodesign data unavailable |  |  | I.S. EN 13141 |  | I.S. EN 13141
#VALUE! | #N/A | #N/A | #N/A | #N/A | <-Applicable values -> |  |  |  | #N/A
#VALUE!
#VALUE!
Valid space heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B12
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G11
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G12
Space Heating Test Standard | I.S. EN 14825 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B14
Space Heating served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Note on A31: 1 and only one means a valid heat pump is selected

## WaterStandardsID_1
Water heat pump type |  |  | Diagnostics cell: Air to Water Electricity Ecodesign applies and/or ecodesign data available I.S. EN 16147 | Water heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  |  | Water heating valid standards | Heat Pump # | 1
Selector | Type of heat pump | Electric / Gas(GAHP) | Ecodesign applicable? | I.S. EN 16147 | I.S. EN 14511 | I.S. EN 255-3 | I.S. EN 13203-6 | I.S. EN 14825/14511
1 | Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
| Brine to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
| Water to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
| Exhaust Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
| Direct exchange (DX) | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
| Air to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
| Brine to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
| Water to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
| Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
| Brine to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
| Water to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
| Exhaust Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
| Direct exchange (DX) | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  |  | I.S. EN 14511
| Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | <-Applicable values -> |  |  |  |  | I.S. EN 16147 I.S. EN 14825/14511
Valid water heat pump type selected.
Valid water heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | Air to Water | $HP_ | #VALUE! | $HP_1.B65
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | Not low temperature heat pump | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | Electricity | $HP_ | #VALUE! | $HP_1.G63
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | Ecodesign applies and/or ecodesign data available | $HP_ | #VALUE! | $HP_1.G64
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | I.S. EN 16147 | $HP_ | #VALUE! | $HP_1.B68
Space Heating served by HP | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | 1 | $HP_ | #VALUE! | $HP_1.N12
Error for water heating using low temp HP? |  | #VALUE! | #VALUE! |  | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A32
Note on A17: 1 and only one (no more no less) means a valid heat pump is selected

## WaterStandardsID_2
Water heat pump type |  |  | #VALUE! | Water heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  |  | Water heating valid standards | Heat Pump # | 2
Selector | Type of heat pump | Electric / Gas(GAHP) | Ecodesign applicable? | I.S. EN 16147 | I.S. EN 14511 | I.S. EN 255-3 | I.S. EN 13203-6 | I.S. EN 14825/14511
#VALUE! | Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Brine to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Water to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Exhaust Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Direct exchange (DX) | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Air to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Water to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Brine to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Water to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Exhaust Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Direct exchange (DX) | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  |  | I.S. EN 14511
| #N/A | #N/A | #N/A | <-Applicable values -> |  |  |  |  | #N/A
#VALUE!
#VALUE!
#VALUE!
Valid water heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B65
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G63
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G64
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Space Heating served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Error for water heating using low temp HP? |  | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A32
Note on A17: 1 and only one (no more no less) means a valid heat pump is selected

## WaterStandardsID_3
Water heat pump type |  |  | #VALUE! | Water heating valid options (where blank, that standard is not applicable to selected heat pump) |  |  |  |  | Water heating valid standards | Heat Pump # | 3
Selector | Type of heat pump | Electric / Gas(GAHP) | Ecodesign applicable? | I.S. EN 16147 | I.S. EN 14511 | I.S. EN 255-3 | I.S. EN 13203-6 | I.S. EN 14825/14511
#VALUE! | Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Brine to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Water to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Exhaust Air to Water | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Direct exchange (DX) | Electricity | Ecodesign applies and/or ecodesign data available | I.S. EN 16147 |  |  |  | I.S. EN 14825/14511 | I.S. EN 16147 I.S. EN 14825/14511
#VALUE! | Air to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Brine to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Water to Water | Gas fired (GAHP) | Ecodesign applies and/or ecodesign data available |  |  |  | I.S. EN 13203-6 |  | I.S. EN 13203-6
#VALUE! | Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Brine to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Water to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Exhaust Air to Water | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 | I.S. EN 255-3 |  |  | I.S. EN 14511 I.S. EN 255-3
#VALUE! | Direct exchange (DX) | Electricity | Ecodesign doesn't apply and ecodesign data unavailable |  | I.S. EN 14511 |  |  |  | I.S. EN 14511
| #N/A | #N/A | #N/A | <-Applicable values -> |  |  |  |  | #N/A
#VALUE!
#VALUE!
#VALUE!
Valid water heat pump type selected.
Heatpump replication autoselect | Heat pump #1 | Heat pump #2 | Heat pump #3
HP tab | 1 | 2 | 3 | This HP | Tab | Cell (everything to the right of the tab name) | Heat pump 1 source cell name as text
Type of heat pump | Air to Water | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B65
Is this a Low Temperature Heat Pump? | Not low temperature heat pump | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G10
Is this heat pump electric or gas (GAHP)? | Electricity | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G63
What is the status of this heat pump regarding Ecodesign data? | Ecodesign applies and/or ecodesign data available | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.G64
Water Heating Test Standard | I.S. EN 16147 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.B68
Space Heating served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N10
Hot Water served by HP | 1 | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N11
Same HP for Space and Water Heating | TRUE | #VALUE! | #VALUE! | #VALUE! | $HP_ | #VALUE! | $HP_1.N12
Error for water heating using low temp HP? |  | #VALUE! | #VALUE! | #VALUE! | $SpaceStandardsID_ | #VALUE! | $SpaceStandardsID_1.A32
Note on A17: 1 and only one (no more no less) means a valid heat pump is selected

## Meteorological data
| 16 | Design Temperature |  |  |  | DHW Energy kWh
Taken as 16 based on EN14825/EN12309-6
Outdoor temperature bin (deg C) | Name IRL_Dublin_IWEC2.epw Description IWEC2- ASHRAE Latitude 53.43000031 Longitude -6.25 Time Zone -0.419999987 Year 2000 Ground Source Temperature 11.97182465 Altitude 0 Number of hours per bin | Cumulative Hrs | Heating Degree Hrs | Cumulative heating Degree Hrs | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8
-12 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0
-5 | 0 | 0 | 0 | 0 | 0 | 0
-4 | 0 | 0 | 0 | 0 | 0 | 0
-3 | 4 | 4 | 76 | 76 | 0.0013629 | 0.00045662
-2 | 14 | 18 | 252 | 328 | 0.0045191 | 0.0015982
-1 | 44 | 62 | 748 | 1076 | 0.013414 | 0.0050228
0 | 112 | 174 | 1792 | 2868 | 0.032136 | 0.012785
1 | 146 | 320 | 2190 | 5058 | 0.039273 | 0.016667
2 | 222 | 542 | 3108 | 8166 | 0.055736 | 0.025342
3 | 323 | 865 | 4199 | 12365 | 0.075301 | 0.036872
4 | 400 | 1265 | 4800 | 17165 | 0.086079 | 0.045662
5 | 446 | 1711 | 4906 | 22071 | 0.087979 | 0.050913
6 | 545 | 2256 | 5450 | 27521 | 0.097735 | 0.062215
7 | 603 | 2859 | 5427 | 32948 | 0.097323 | 0.068836
8 | 658 | 3517 | 5264 | 38212 | 0.0944 | 0.075114
9 | 681 | 4198 | 4767 | 42979 | 0.085487 | 0.07774
10 | 639 | 4837 | 3834 | 46813 | 0.068755 | 0.072945
11 | 660 | 5497 | 3300 | 50113 | 0.059179 | 0.075342
12 | 610 | 6107 | 2440 | 52553 | 0.043757 | 0.069635
13 | 582 | 6689 | 1746 | 54299 | 0.031311 | 0.066438
14 | 481 | 7170 | 962 | 55261 | 0.017252 | 0.054909
15 | 502 | 7672 | 502 | 55763 | 0.0090024 | 0.057306
16 | 383 | 8055 | 0 |  |  | 0.043721
17 | 259 | 8314 |  |  |  | 0.029566
18 | 170 | 8484 |  |  |  | 0.019406
19 | 112 | 8596 |  |  |  | 0.012785
20 | 67 | 8663 |  |  |  | 0.0076484
21 | 37 | 8700 |  |  |  | 0.0042237
22 | 27 | 8727 |  |  |  | 0.0030822
23 | 20 | 8747 |  |  |  | 0.0022831
24 | 13 | 8760 |  |  |  | 0.001484
25 | 0 | 8760 |  |  |  | 0
26 | 0 | 8760 |  |  |  | 0
27 | 0 | 8760 |  |  |  | 0
28 | 0 | 8760 |  |  |  | 0
29 | 0 | 8760 |  |  |  | 0
30 | 0 | 8760 |  |  |  | 0
31 | 0 | 8760 |  |  |  | 0
32 | 0 | 8760 |  |  |  | 0
33 | 0 | 8760 |  |  |  | 0
34 | 0 | 8760 |  |  |  | 0
35 | 0 | 8760 |  |  |  | 0
0