## SEAI Calculator
Steam Trap energy credit determination using SEAI calculator
Use Napiers Equation :Steam flow through a sharp edged orifice
W = 0.24725 * Pa * D2 | SI unit method |  | Input needed |  |  | Assumptions | 24.24 | Napiers Constant (Imperial units)
W = 24.24 * Pa * D2 | Imperial unit method | [5 empty] | 0.24725 | Napiers Constant (SI units)
|  |  | Calculated Data |  |  |  | 1.0132 | Patm is Atmospheric pressure in bar
Where | [6 empty] | 14.6959 | Patm is Atmospheric pressure in psi
W= | leakage rate in kg/hr or lb/hr (SI/Imp) |  | Calculated energy savings |  |  | Primary energy kWh/tonne | 750 | From measured site data based on minimum of 12 months recent data.
0.24725 | Napier's Constant using SI units approach
24.24 | Napier's Constant using Imperial approach
Pa = | Absolute pressure drop across the orifice in bar/psig (SI/Imperial)
D= | Diameter of leaking orifice mm/inches (SI/Imperial)
Steam trap Audit Report | Steam Tag Number | Steam trap manufacturer | Pressure [barg] | Pressure [psia] | Trap Orifice [mm] | Trap Orifice [in] | Leakage rate in Imperial units [lb/hr] | Leakage rate in SI units [kg/hr] | Annual hours | Theoretical leakage [kg/yr] | Correction factor [%] | Calculated steam leakage [tonnes/year] | Primary Site Energy (kWh) input fuel per tonne of steam (kWh/tonne)
Input here in green cells below and add or delete rows as needed. |  |  | Operating steam system pressure | 14.5038 conversion multiplier | Input here in green cells | 25.4 conversion multiplier | Napiers formule | Napiers formule | Operating steam system annual hours. | Multiply Leakage rate by annual hours | Assume here @ 50% | Result for leakage rate | Site SEC in kWh/tonnes
Stream Trap Audit Report dated ??? |  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 50% | 0 | 0
[9 empty] | Steam Trap Energy saved in kWh/annum |  |  |  | 0

## Worked Example
Worked example : Steam Trap energy credit determination involving four steam traps replaced as based on Steam Trap Audit carried out on 12th March 2022.
Use Napiers Equation :Steam flow through a sharp edged orifice
W = 0.24725 * Pa * D2 | SI unit method |  | Input needed |  |  | Assumptions | 24.24 | Napiers Constant (Imperial units)
W = 24.24 * Pa * D2 | Imperial unit method | [5 empty] | 0.24725 | Napiers Constant (SI units)
|  |  | Calculated Data |  |  |  | 1.0132 | Patm is Atmospheric pressure in bar
Where | [6 empty] | 14.6959 | Patm is Atmospheric pressure in psi
W= | leakage rate in kg/hr or lb/hr (SI/Imp) |  | Calculated energy savings |  |  | Primary energy kWh/tonne | 750 | From measured site data based on minimum of 12 months recent data.
0.24725 | Napier's Constant using SI units approach
24.24 | Napier's Constant using Imperial approach
Pa = | Absolute pressure drop across the orifice in bar/psig (SI/Imperial)
D= | Diameter of leaking orifice mm/inches (SI/Imperial)
Steam trap Audit Report | Steam Tag Number | Steam trap manufacturer | Pressure [barg] | Pressure [psia] | Trap Orifice [mm] | Trap Orifice [in] | Leakage rate [lb/hr] | Leakage rate [kg/hr] | Annual hours | Theoretical leakage [kg/annum] | Correction factor [%] | Calculated steam leakage [tonnes/year] | Primary Site Energy (kWh) fuel saving per annum
Input here in green cells below |  |  | Operating steam system pressure | 14.5038 conversion multiplier | Input here in green cells | 25.4 conversion multiplier | Napiers formula calculation | 2.20462 conversion factor | Operating steam system annual hours. | Multiply Leakage rate by annual hours | Assume here @ 50% | Result for leakage rate | This is based on site energy SEC of 750kWh/tonne as per input data in cell I7.
Stream Trap Audit Report dated 12th March 2022 | 15 | ABC Supplier | 12 | 174.0456 | 3 | 0.11811 | 63.8227 | 28.9579 | 7200 | 208496.9783 | 50% | 104.2485 | 78186.3669
| 34 | ABC Supplier | 12 | 174.0456 | 9 | 0.35433 | 574.4042 | 260.6212 | 5000 | 1303106.1145 | 50% | 651.5531 | 488664.7929
| 39 | ABC Supplier | 12 | 174.0456 | 9 | 0.35433 | 574.4042 | 260.6212 | 7200 | 1876472.8049 | 50% | 938.2364 | 703677.3018
| 56 | ABC Supplier | 12 | 174.0456 | 16 | 0.62992 | 1815.4009 | 823.6918 | 8400 | 6919010.836 | 50% | 3459.5054 | 2594629.0635
[9 empty] | Steam Trap Energy saved in kWh/annum |  |  |  | 3865157.5251